## Instr.
General instruction mentioned below to fill the sheet and Calculate savings.
Please follow the below steps:
Site Survey & Collection of the AC details
Step 1
Survey shall be done for all building in project scope.
Each Building, each room details to collect like Zone Name / No, Building Name / No,Floor No, Space type / Use, AC QTY, AC operation and area served(m2) etc.
Collect Nameplate Picture of each unique AC model (Both Indoor and same connected Outdoor) AC's.
Including equipment Type and capacity (Window / Wallmounted/ Cassette / Floorstand / Ceiling etc ) Make,Model Number ,Compressor Type (Inverter or Non - Inverter ) etc.
Total Quantity of Each unique model number of each equipment type.
Survey the AC compressor type in detailed and avoid considering inverter AC systems in replacement scope.
Do not include AC units in housing or residential buildings for savings calculation.
Fill out the Sheet "OH"
Step 2 |  | Fill these cells as instructed below.
Do not change any values on these cells.
Fiilout Region , District - Identify the areas, location, building names, usage for all buildings under the scope.This will be reflected in the savings sheet.
Sheet shall fill only with unique information like Building Name ,unique space type and unique operation hours for the AC.
If the building has multiple ac's with same space type and same operation hours fill it once under the building Name.
Identify the operating hours of AC from 00:00:00 AM to 23:59:00 PM for all areas based on the letter from the entity or site collected information.
Fillout no of days AC working per week & no of weeks AC working per year.
If AC's are not operating during vacation / off days, fill only working weeks and mention which weeks are not in operation.
Make sure operation hours are filled for AC running hours of that space.
Use of EFLH Calculator
EFLH calculator to used to calculate the AC fullload running hours based on the hours of operation.
Each region has its own EFLH tool. Be sure to use the calculator specific to your project's location.
For Mosque use std EFLH value mentioned in tool.
Fill this calculated value in AC_OH sheet which will reflect in savings sheet.
Eg. For OH from 16:00PM to 8:00AM, enter data 16:00PM to 23:59PM and Then 00:00AM to 8:00AM ,sum both value get total EFLH.
Sheet "Aprvd Project Units"
This part shall be filled out as per the Material Submittal proposal.
Provide AC valid SASO Label & certificate of each proposed model.
Ensure the supplier has the required stock.
SASO and Datasheet details should be renamed as per model description as below.
Window Zamil 1.5TR SEER 6.51
(Type: Window or split) (Make) (Tonnage) (SEER: SEER Value)
Refer Project_AC List for all approved model from multiple suppliers, if not available it can add in the last row for that capacity and Submit SASO.
Fill out the Sheet "AC_Savings"
Step 3
Fill these cells based on site collected information as instructed below.
Do not change any values on these cells.
| EFLH | all values will be automatically generated.
| Capacity Check | Make sure each selected models for Project units should be within 10% of original capacity.
| % Savings | Make sure % of Savings is greater than or equal 15%
| AC Type Match | AC type selection for baseline and replacement must match,refer column "AH" to verify.
Select "Building Name" from dropdown list, followed by location description which contains space type ,these location are only for the selcted building, other details will be autogenerated linked to OH table.
Fillout above selected space Floor no and existing AC area served in sq. meter.
Fillout existing AC qty in that space. Qty can be merged together if the space type, AC opertaion timing and existing model specification are same.
Now fill surveyed AC details for that space , select Equipment type, Make,Size category and Model no from dropdown list. Equivalent model selection shall autogenerate for that baseline unit. If Model no not available in the "Old_Model_Registry" share the Nameplate picture to Tarshid Technical team to add in the list.
Make sure Column "N" to Column "Q" selection are in ascending order to avoid error or Null value.
Now fill the Proposed AC details for that space, Select equipment description from dropdown list.
Very important: Make sure all existing AC's are (+-) 10% range of New Project AC's , if Not please submit MS with new capacity within range of existing ac BTUH.
Inverter AC must not include in scope of replacement , hence selection not required.
Refer "Aprvd Baseline Unit"
Do not change / enter any values on these cells.
This is the information of the equivalent baseline (old) existing units for selection and use for savings calculation.
Window and Split units that have namplate and datasheets.
Provide Nameplate Pic and exact Datasheet in order to add in this baseline list.
Refer "Old_Model_Registry"
Do not change / enter any values on these cells.
This is the database of the (old) existing units for selection and use for savings calculation.
If any model not found in this database , provide nameplate picture to add here.
Picture should be readable combined with connected Indoor and Outdoor with Nameplate as "shown in Pic".
Savings Sheet – Version Update as of 26th Nov 2025

## AC_Savings
Sl No. | Building Name | Building Description | Zone/Building No. | Space Type | Operating hours refrence | Operating hours (Start time) | Operating hours ( End time) | Calculated EFLH | Floor Number | Area Served (m2) | M2/Ton | Qty | Equipment Type | Make | Size Category | Model No | Surveyed Unit Description | Equivalent AC Model Description | T1 BTU | T1 EER | Equivalent SEER | New Unit Description | Model Number | Brand/ Make | Capacity T1 Btu/h *Shall be within 10% of original capacity | Proposed SEER | Savings kWh | Baseline kWh | Savings % | Capacity Check | Payback (in Yr.) | In Repl. Scope (Yes / No) | AC Type Match Check

## OH
For Coding Use do not erase | #Sl No | Region | Entity Name | Building Location (District / Street) | Zone/Building Number | Building Coordinates | Building Name | Description (Combined value) | Space type / Category | AC Operating hours (Start time) | AC Operating hours ( End time) | Working days per week | Weeks per year | Operating hours reference | Operating hours per year | EFLH

## Aprvd Project Unit
S.N | Description | Unit Cost | labor Cost | Total Cost | Equipment Type | Make | Model No (ID/ OD) | T1 BTU | TR | SEER | C/H | Reference SASO Certificate | Reference Datasheet

## Data_Check
Sl No. | Zone / Building Number | Equipment Type | Make | Size Category | Model No | Surveyed Unit Description | Compressor Type | TR | T1 BTU | T1 EER | Calculated SEER | Equivalent AC Model Description | Make | Model No (ID/ OD) | T1 BTU | T1 EER | Equivalent SEER | New Unit Description | Model Number | Brand/ Make | Capacity T1 Btu/h *Shall be within 10% of original capacity | CooL/Heat | Proposed SEER | Capacity Check | Savings% | Capacity Check | Model List | OH | OH

## Aprvd Baseline Unit
S.N | Description | Equipment Type | Make | Model No (ID/ OD) | T1 BTU | T1 W | T1 EER | T3 BTU | T3 W | T3 EER | Equivalent SEER | Reference Nameplate Photo | Reference Datasheet
1 | Split_Wall_Mounted LG 0.95TR SEER 7.9 | Split_Wall_Mounted | LG | S122DH | 11498 | 1200 | 9.58 | 8871 | 1400 | 6.34 | 7.9 | Same as description | Same as description
2 | Split_Wall_Mounted LG 0.95TR SEER 8.3 | Split_Wall_Mounted | LG | S122SH / GS-H122E0B1 | 11498.4362 | 1200 | 9.58 | 10235.9966 | 1400 | 7.31 | 8.3 | Same as description | Same as description
3 | Split_Wall_Mounted Carrier 0.96TR SEER 10.37 | Split_Wall_Mounted | Carrier | 42QHF012H | 11500 | 940 | 12.23 | 9700 | 1110 | 8.74 | 10.37 | Same as description | Same as description
4 | Split_Wall_Mounted Royal Temp 1TR SEER 6.59 | Split_Wall_Mounted | Royal Temp | MIS-120-C | 12000 | 1518 | 7.91 | 9480 | 1755 | 5.4 | 6.59 | Same as description | Same as description
5 | Split_Ceiling_Cassette Carrier 1.33TR SEER 10.51 | Split_Ceiling_Cassette | Carrier | 42KTD018HS | 16000 | 1330 | 12.03 | 15000 | 1610 | 9.32 | 10.51 | Same as description | Same as description
6 | Split_Wall_Mounted Chigo 1.38TR SEER 9.88 | Split_Wall_Mounted | Chigo | CZS-18CH | 16675 | 1450 | 11.5 | 14362 | 1670 | 8.6 | 9.88 | Same as description | Same as description
7 | Split_Wall_Mounted LG 1.41TR SEER 6.94 | Split_Wall_Mounted | LG | S182DH | 17025.8743 | 2100 | 8.11 | 14671.5951 | 2450 | 5.99 | 6.94 | Same as description | Same as description
8 | Split_Wall_Mounted York 1.42TR SEER 9.83 | Split_Wall_Mounted | York | YE6HC18SH/YE6SD180SHZW41 | 17040 | 1478 | 11.53 | 15097 | 1819 | 8.3 | 9.83 | Same as description | Same as description
9 | Split_Wall_Mounted LG 1.45TR SEER 9.84 | Split_Wall_Mounted | LG | B1828H N51 | 17469.4342 | 1510 | 11.57 | 14978.675 | 1800 | 8.32 | 9.84 | Same as description | Same as description
10 | Split_Wall_Mounted LG 1.46TR SEER 7.56 | Split_Wall_Mounted | LG | S182DC u51 | 17500 | 2000 | 8.75 | 15300 | 2300 | 6.65 | 7.56 | Same as description | Same as description
11 | Split_Wall_Mounted LG 1.46TR SEER 7.28 | Split_Wall_Mounted | LG | S182SC / LSUC1825SB0 | 17503 | 2050 | 8.54 | 15183 | 2450 | 6.2 | 7.28 | Same as description | Same as description
12 | Split_Wall_Mounted LG 1.46TR SEER 7.57 | Split_Wall_Mounted | LG | S182DC N51 | 17503.5542 | 2000 | 8.75 | 15353.9949 | 2300 | 6.68 | 7.57 | Same as description | Same as description
13 | Split_Wall_Mounted LG 1.46TR SEER 9.8 | Split_Wall_Mounted | LG | A1828P nco | 17503.5542 | 1520 | 11.52 | 15012.795 | 1810 | 8.29 | 9.8 | Same as description | Same as description
14 | Split_Wall_Mounted Zamil 1.47TR SEER 9.8 | Split_Wall_Mounted | Zamil | ADO18CHXOW | 17698.0381 | 1532 | 11.55 | 14797.8391 | 1783 | 8.3 | 9.8 | Same as description | Same as description
15 | Split_Wall_Mounted LG 1.47TR SEER 10.15 | Split_Wall_Mounted | LG | T182NC NC0 / LS Q182CNC0 | 17742 | 1500 | 11.83 | 15286 | 1740 | 8.79 | 10.15 | Same as description | Same as description
16 | Split_Wall_Mounted Ugine 1.48TR SEER 10.23 | Split_Wall_Mounted | Ugine | UASG18H | 17800 | 1465 | 12.15 | 14500 | 1696 | 8.55 | 10.23 | Same as description | Same as description
17 | Split_Wall_Mounted Zamil 1.49TR SEER 10.52 | Split_Wall_Mounted | Zamil | MAZ18CCXAD1 | 17998.294 | 1440 | 12.5 | 15899.9147 | 1849 | 8.6 | 10.52 | Same as description | Same as description
18 | Split_Wall_Mounted Zamil 1.49TR SEER 10.96 | Split_Wall_Mounted | Zamil | ADO18CHX0D | 17998.294 | 1379 | 13.05 | 15295.9909 | 1700 | 9 | 10.96 | Same as description | Same as description
19 | Split_Ceiling_Cassette LG 1.5TR SEER 8.05 | Split_Ceiling_Cassette | LG | LT-C182ELE0 | 18000 | 1970 | 9.14 | 16002.2747 | 2150 | 7.44 | 8.05 | Same as description | Same as description
20 | Split_Wall_Mounted LG 1.5TR SEER 10.46 | Split_Wall_Mounted | LG | NF182H2 | 18000 | 1452 | 12.4 | 15300 | 1759 | 8.7 | 10.46 | Same as description | Same as description
21 | Split_Wall_Mounted LG 1.5TR SEER 8.40 | Split_Wall_Mounted | LG | LS-H182TNB0 | 18000 | 1860 | 9.68 | 16002.2747 | 2150 | 7.44 | 8.4 | Same as description | Same as description
22 | Split_Wall_Mounted General 1.5TR SEER 10.16 | Split_Wall_Mounted | General | GC-18KFC | 18000 | 1500 | 12 | 15500 | 1824 | 8.5 | 10.16 | Same as description | Same as description
23 | Split_Wall_Mounted Mando 1.5TR SEER 10.35 | Split_Wall_Mounted | Mando | MP-SER-18C | 18000 | 1469 | 12.25 | 15500 | 1802 | 8.6 | 10.35 | Same as description | Same as description
24 | Split_Wall_Mounted Unix 1.5TR SEER 10.16 | Split_Wall_Mounted | Unix | Omr/split 18H | 18000 | 1500 | 12 | 15500 | 1824 | 8.5 | 10.16 | Same as description | Same as description
25 | Split_Wall_Mounted GREE 1.5TR SEER 9.98 | Split_Wall_Mounted | GREE | GWC18QD-D3NTB4D/I | 18000 | 1525 | 11.8 | 14900 | 1773 | 8.4 | 9.98 | Same as description | Same as description
26 | Split_Wall_Mounted Royal Temp 1.5TR SEER 7.67 | Split_Wall_Mounted | Royal Temp | MIS-180-HP | 18000 | 2045 | 8.8 | 15732 | 2280 | 6.9 | 7.67 | Same as description | Same as description
27 | Split_Wall_Mounted Carrier 1.5TR SEER 10.95 | Split_Wall_Mounted | Carrier | 42SXC180 | 18000 | 1379 | 13.05 | 15000 | 1667 | 9 | 10.95 | Same as description | Same as description
28 | Split_Wall_Mounted Gree 1.5TR SEER 7.03 | Split_Wall_Mounted | Gree | GWC18MC | 18083 | 2250 | 8.04 | 16200 | 2550 | 6.35 | 7.03 | Same as description | Same as description
29 | Split_Wall_Mounted Cooline 1.5TR SEER 10.25 | Split_Wall_Mounted | Cooline | TAL18CHXED | 18100 | 1496 | 12.1 | 15470 | 1800 | 8.59 | 10.25 | Same as description | Same as description
30 | Split_Wall_Mounted LG 1.52TR SEER 8.15 | Split_Wall_Mounted | LG | Y182SH / GS-H1825SA4 | 18254.1939 | 1900 | 9.61 | 15183.3949 | 2200 | 6.9 | 8.15 | Same as description | Same as description
31 | Split_Wall_Mounted LG 1.52TR SEER 8.15 | Split_Wall_Mounted | LG | Y182NH / GS-H1825SA4 | 18254.1939 | 1900 | 9.61 | 15183.3949 | 2200 | 6.9 | 8.15 | Same as description | Same as description
32 | Split_Wall_Mounted LG 1.53TR SEER 8.30 | Split_Wall_Mounted | LG | S18TQC / HSNC186C4B0 | 18400 | 1919 | 9.59 | 16200 | 2218 | 7.3 | 8.3 | Same as description | Same as description
33 | Split_Wall_Mounted Mando 1.53TR SEER 10.38 | Split_Wall_Mounted | Mando | F23TP-18CT | 18400 | 1484 | 12.4 | 15300 | 1800 | 8.5 | 10.38 | Same as description | Same as description
34 | Split_Wall_Mounted Okia 1.53TR SEER 10.37 | Split_Wall_Mounted | Okia | OKA-18CJ | 18400 | 1510 | 12.19 | 15800 | 1800 | 8.78 | 10.37 | Same as description | Same as description
35 | Split_Wall_Mounted LG 1.54TR SEER 8.14 | Split_Wall_Mounted | LG | Y182SC / GS-C1825SA4 | 18561 | 1950 | 9.52 | 16036 | 2300 | 6.97 | 8.14 | Same as description | Same as description
36 | Split_Wall_Mounted Daikin 1.55TR SEER 7.08 | Split_Wall_Mounted | Daikin | RY18HEVLK / FTY18HEVLK | 18650 | 2260 | 8.25 | 16100 | 2630 | 6.12 | 7.08 | Same as description | Same as description
37 | Split_Wall_Mounted LG 1.74TR SEER 8.20 | Split_Wall_Mounted | LG | Y242NH / GS-H2425SA4 | 20949.673 | 2200 | 9.52 | 18254.1939 | 2550 | 7.16 | 8.2 | Same as description | Same as description
38 | Split_Wall_Mounted LG 1.74TR SEER 9.84 | Split_Wall_Mounted | LG | B2427H / DSNH24257B1 | 20949.673 | 1820 | 11.51 | 18936.5937 | 2280 | 8.31 | 9.84 | Same as description | Same as description
39 | Split_Wall_Mounted LG 1.74TR SEER 9.84 | Split_Wall_Mounted | LG | B2424H | 20949.673 | 1820 | 11.51 | 18936.5937 | 2280 | 8.31 | 9.84 | Same as description | Same as description
40 | Split_Wall_Mounted LG 1.75TR SEER 8.20 | Split_Wall_Mounted | LG | Y242SH N54 | 20949.673 | 2200 | 9.52 | 18254.1939 | 2550 | 7.16 | 8.2 | Same as description | Same as description
41 | Split_Wall_Mounted LG 1.74TR SEER 8.17 | Split_Wall_Mounted | LG | X242EC | 20983.793 | 2200 | 9.54 | 18254.1939 | 2600 | 7.02 | 8.17 | Same as description | Same as description
42 | Split_Wall_Mounted Arrow 1.75TR SEER 10.39 | Split_Wall_Mounted | Arrow | RO-24CBA22-H | 21000 | 1710 | 12.28 | 17900 | 2060 | 8.69 | 10.39 | Same as description | Same as description
43 | Split_Wall_Mounted Giant 1.75TR SEER 10.36 | Split_Wall_Mounted | Giant | GIANT-24C | 21000 | 1750 | 12 | 18900 | 2100 | 9 | 10.36 | Same as description | Same as description
44 | Split_Wall_Mounted Carrier 1.75TR SEER 7.63 | Split_Wall_Mounted | Carrier | 38HQR24US30-04 | 21000 | 2400 | 8.75 | 18500 | 2700 | 6.85 | 7.63 | Same as description | Same as description
45 | Split_Ceiling_Cassette LG 1.75TR SEER 7.36 | Split_Ceiling_Cassette | LG | LTNC242QLE0 | 21017.913 | 2470 | 8.51 | 18697.7538 | 2900 | 6.45 | 7.36 | Same as description | Same as description
46 | Split_Ceiling_Cassette Mitsubishi 1.76TR SEER 6.74 | Split_Ceiling_Cassette | Mitsubishi | FDTN257HEPA | 21154.3929 | 2680 | 7.89 | 17742.3941 | 3050 | 5.82 | 6.74 | Same as description | Same as description | Yes | Yes
47 | Split_Wall_Mounted LG 1.79TR SEER 7.34 | Split_Wall_Mounted | LG | S242DC N51 | 21495.5928 | 2500 | 8.6 | 18765.9937 | 3000 | 6.26 | 7.34 | Same as description | Same as description
48 | Split_Wall_Mounted Crown 1.79TR SEER 10.33 | Split_Wall_Mounted | Crown | CROWN 24C | 21500 | 1770 | 12.15 | 18600 | 2130 | 8.73 | 10.33 | Same as description | Same as description
49 | Split_Wall_Mounted Carrier 1.79TR SEER 10.35 | Split_Wall_Mounted | Carrier | 38QKA0243 | 21500 | 1762 | 12.2 | 18500 | 2126 | 8.7 | 10.35 | Same as description | Same as description
50 | Split_Wall_Mounted Carrier 1.79TR SEER 8.31 | Split_Wall_Mounted | Carrier | 38MQR18US33-04 | 21500 | 2240 | 9.6 | 19000 | 2600 | 7.31 | 8.31 | Same as description | Same as description
51 | Split_Wall_Mounted Carrier 1.81TR SEER 7.91 | Split_Wall_Mounted | Carrier | 38HKR24US30-04 | 21750 | 2400 | 9.06 | 19500 | 2750 | 7.09 | 7.91 | Same as description | Same as description
52 | Split_Wall_Mounted LG 1.82TR SEER 9.79 | Split_Wall_Mounted | LG | B242PC | 21870.9127 | 1900 | 11.51 | 18970.7137 | 2290 | 8.28 | 9.79 | Same as description | Same as description
53 | Split_Wall_Mounted Zamil 1.83TR SEER 7.51 | Split_Wall_Mounted | Zamil | MLZ24CHIXFTR | 21997.1567 | 2558 | 8.6 | 19499.5735 | 2868 | 6.8 | 7.51 | Same as description | Same as description
54 | Split_Wall_Mounted LG 1.83TR SEER 10.27 | Split_Wall_Mounted | LG | NS242H2 | 22000 | 1818 | 12.1 | 18500 | 2127 | 8.7 | 10.27 | Same as description | Same as description
55 | Split_Wall_Mounted Gree 1.83TR SEER 10.17 | Split_Wall_Mounted | Gree | GWC24AGE-D3NTA1A/O | 22000 | 1818 | 12.1 | 18300 | 2178 | 8.4 | 10.17 | Same as description | Same as description
56 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43 | Split_Wall_Mounted | Supergeneral | KSGS245GER | 22000 | 1781 | 12.35 | 18400 | 2114 | 8.7 | 10.43 | Same as description | Same as description
57 | Split_Ceiling_Cassette LG 1.83TR SEER 10.59 | Split_Ceiling_Cassette | LG | ATNQ24GPLT2 | 22000 | 1770 | 12.43 | 20000 | 2260 | 8.85 | 10.59 | Same as description | Same as description
58 | Split_Wall_Mounted Carrier 1.83TR SEER 10.08 | Split_Wall_Mounted | Carrier | 42SKC243-2S | 22000 | 1833 | 12 | 18500 | 2229 | 8.3 | 10.08 | Same as description | Same as description
59 | Split_Wall_Mounted Zamil 1.83TR SEER 10.42 | Split_Wall_Mounted | Zamil | MAZ24CHXAD1 | 22000.5687 | 1781 | 12.35 | 18397.4979 | 2114 | 8.7 | 10.42 | Same as description | Same as description
60 | Split_Wall_Mounted Mando 1.84TR SEER 10.28 | Split_Wall_Mounted | Mando | MP-NF23-24C/H | 22100 | 1804 | 12.25 | 18500 | 2189 | 8.45 | 10.28 | Same as description | Same as description
61 | Split_Wall_Mounted Midea 1.84TR SEER 10.28 | Split_Wall_Mounted | Midea | MSTEP24CRNAG2 | 22100 | 1804 | 12.25 | 18500 | 2189 | 8.45 | 10.28 | Same as description | Same as description
62 | Split_Wall_Mounted Carrier 1.84TR SEER 10.16 | Split_Wall_Mounted | Carrier | 38HVBS024-3032B | 22100 | 1830 | 12.08 | 19300 | 2320 | 8.32 | 10.16 | Same as description | Same as description
63 | Split_Wall_Mounted LG 1.87TR SEER 7.14 | Split_Wall_Mounted | LG | S242SHU51 | 22519.1925 | 2640 | 8.53 | 18936.5937 | 3250 | 5.83 | 7.14 | Same as description | Same as description
64 | Split_Wall_Mounted LG 1.91TR SEER 7.54 | Split_Wall_Mounted | LG | S242MH | 22996.8723 | 2630 | 8.74 | 20062.5533 | 3035 | 6.61 | 7.54 | Same as description | Same as description
65 | Split_Wall_Mounted LG 1.58TR SEER 7.54 | Split_Wall_Mounted | LG | S242NH ST0 | 22996.8723 | 2630 | 8.74 | 20062.5533 | 3035 | 6.61 | 7.54 | Same as description | Same as description
66 | Split_Wall_Mounted Fisher 1.92TR SEER 10.16 | Split_Wall_Mounted | Fisher | FSAC-FT24CERAN | 23000 | 1917 | 12 | 19800 | 2329 | 8.5 | 10.16 | Same as description | Same as description
67 | Split_Wall_Mounted Carrier 1.92TR SEER 9.83 | Split_Wall_Mounted | Carrier | 38PQR24US33-08 | 23000 | 1991 | 11.55 | 20000 | 2410 | 8.3 | 9.83 | Same as description | Same as description
68 | Split_Wall_Mounted Carrier 1.92TR SEER 9.83 | Split_Wall_Mounted | Carrier | 38PQS24US33-01 | 23000 | 1990 | 11.56 | 20000 | 2410 | 8.3 | 9.83 | Same as description | Same as description
69 | Split_Wall_Mounted Carrier 1.92TR SEER 9.83 | Split_Wall_Mounted | Carrier | 42QHMT24N-308J | 23000 | 1991 | 11.55 | 20000 | 2410 | 8.3 | 9.83 | Same as description | Same as description
70 | Split_Ceiling_Cassette Zamil 1.94TR SEER 10.35 | Split_Ceiling_Cassette | Zamil | SCZ24CHAXCD1 | 23300 | 1900 | 12.26 | 19800 | 2300 | 8.61 | 10.35 | Same as description | Same as description
71 | Split_Wall_Mounted Zamil 2TR SEER 6.69 | Split_Wall_Mounted | Zamil | ADX24EHAXFQ | 23491 | 2975 | 7.9 | 18994 | 3325 | 5.71 | 6.69 | Same as description | Same as description
72 | Split_Wall_Mounted Zamil 1.95TR SEER 8.11 | Split_Wall_Mounted | Zamil | ADU24CHAXFV | 23498.4362 | 2460 | 9.55 | 20100.0853 | 2935 | 6.85 | 8.11 | Same as description | Same as description
73 | Split_Ceiling_Cassette Carrier 1.96TR SEER 10.25 | Split_Ceiling_Cassette | Carrier | 42KTD024HS | 23500 | 1950 | 12.05 | 20000 | 2300 | 8.7 | 10.25 | Same as description | Same as description
74 | Split_Ceiling_Cassette Carrier 1.97TR SEER 10.37 | Split_Ceiling_Cassette | Carrier | 42QTD024HSN | 23600 | 1927 | 12.25 | 20000 | 2300 | 8.7 | 10.37 | Same as description | Same as description
75 | Split_Ceiling_Cassette LG 1.99TR SEER 8.23 | Split_Ceiling_Cassette | LG | LTNC242PLE1 | 23885 | 2500 | 9.55 | 21667 | 3050 | 7.1 | 8.23 | Same as description | Same as description
76 | Split_Wall_Mounted LG 1.99TR SEER 9.80 | Split_Wall_Mounted | LG | A3024HNV0 | 23986.352 | 2080 | 11.53 | 20779.0731 | 2510 | 8.28 | 9.8 | Same as description | Same as description
77 | Split_Wall_Mounted Zamil 1.99TR SEER9.77 | Split_Wall_Mounted | Zamil | ADO24CHXOW | 23996.588 | 2078 | 11.55 | 19299.0752 | 2325 | 8.3 | 9.77 | Same as description | Same as description
78 | Split_Wall_Mounted Zamil 1.99TR SEER9.77 | Split_Wall_Mounted | Zamil | KRC24CDMHJOW | 23996.588 | 2078 | 11.55 | 19298.2656 | 2325 | 8.3 | 9.77 | Same as description | Same as description
79 | Split_Wall_Mounted LG 2TR SEER 7.91 | Split_Wall_Mounted | LG | S242WQ / LSUH2425WM1 | 24000 | 2600 | 9.23 | 19653 | 2840 | 6.92 | 7.91 | Same as description | Same as description
80 | Split_Wall_Mounted DAEWOO 2TR SEER 7.86 | Split_Wall_Mounted | DAEWOO | DSA-240LH-R | 24000 | 2500 | 9.6 | 17496.7302 | 2800 | 6.25 | 7.86 | Same as description | Same as description
81 | Split_Ceiling_Cassette LG 2.0TR SEER 8.33 | Split_Ceiling_Cassette | LG | LT-C242ELE0 | 24000 | 2500 | 9.6 | 21000 | 2830 | 7.42 | 8.33 | Same as description | Same as description
82 | Split_Wall_Mounted Royal Temp 2TR SEER 7.64 | Split_Wall_Mounted | Royal Temp | MIS-240-HP | 24000 | 2727 | 8.8 | 20064 | 2907 | 6.9 | 7.64 | Same as description | Same as description
83 | Split_Wall_Mounted Carrier 2TR SEER 8.60 | Split_Wall_Mounted | Carrier | 42QCF02433 | 24000 | 2450 | 9.8 | 21000 | 2650 | 7.92 | 8.6 | Same as description | Same as description
84 | Split_Wall_Mounted Zamil 2TR SEER 10.39 | Split_Wall_Mounted | Zamil | KRZ26CDACIED | 24055 | 1935 | 12.43 | 19960 | 2353 | 8.48 | 10.39 | Same as description | Same as description
85 | Split_Ceiling_Cassette Mitsubishi 2.02TR SEER 6.93 | Split_Ceiling_Cassette | Mitsubishi | FDTN306CEP | 24225.1919 | 3030 | 8 | 19448.3935 | 3260 | 5.97 | 6.93 | Same as description | Same as description | Yes | Yes
86 | Split_Wall_Mounted MITSUBISHI 2.03TR SEER 7.10 | Split_Wall_Mounted | MITSUBISHI | PK-2.5FLD | 24400 | 3010 | 8.11 | 22700 | 3540 | 6.41 | 7.12 | Same as description | Same as description
87 | Split_Wall_Mounted Zamil 2.11TR SEER7.24 | Split_Wall_Mounted | Zamil | MWZ30CHIXFTQ/KZC30CSIHAMCQ | 25398.9195 | 3050 | 8.33 | 21997.1567 | 3375 | 6.52 | 7.24 | Same as description | Same as description
88 | Split_Wall_Mounted Zamil 2.12TR SEER 8.09 | Split_Wall_Mounted | Zamil | HWU30EHAYFV | 25497.8675 | 2670 | 9.55 | 21099.801 | 3080 | 6.85 | 8.09 | Same as description | Same as description
89 | Split_Wall_Mounted GREE 2.19TR SEER 10.05 | Split_Wall_Mounted | GREE | GWC30QE-D3NTN4A/I | 26300 | 2230 | 11.79 | 22800 | 2680 | 8.51 | 10.05 | Same as description | Same as description
90 | Split_Wall_Mounted LG 2.21TR SEER 7.49 | Split_Wall_Mounted | LG | S322GH | 26545.3512 | 3050 | 8.7 | 23269.8322 | 3570 | 6.52 | 7.49 | Same as description | Same as description
91 | Split_Wall_Mounted LG 2.21TR SEER 8.14 | Split_Wall_Mounted | LG | S3228Q / LS-H322V8C2 | 26613.5911 | 2790 | 9.54 | 23713.3921 | 3450 | 6.87 | 8.14 | Same as description | Same as description
92 | Split_Wall_Mounted LG 2.22TR SEER 8.14 | Split_Wall_Mounted | LG | S3224H NV2 | 26613.5911 | 2790 | 9.54 | 23713.3921 | 3450 | 6.87 | 8.14 | Same as description | Same as description
93 | Split_Wall_Mounted Zamil 2.24TR SEER 10.35 | Split_Wall_Mounted | Zamil | ADO30CHXCD | 26954.791 | 2195 | 12.28 | 23798.6921 | 2800 | 8.5 | 10.35 | Same as description | Same as description
94 | Split_Wall_Mounted LG 2.25TR SEER 7.28 | Split_Wall_Mounted | LG | S322GC SD3 | 26988.911 | 3210 | 8.41 | 23747.5121 | 3690 | 6.44 | 7.28 | Same as description | Same as description
95 | Split_Wall_Mounted Gree 2.25TR SEER 11.11 | Split_Wall_Mounted | Gree | GWC30QF-S3DTB2A/O | 27000 | 2080 | 12.98 | 23200 | 2430 | 9.55 | 11.11 | Same as description | Same as description
96 | Split_Wall_Mounted Okia 2.25TR SEER 10.59 | Split_Wall_Mounted | Okia | OKA-30CH | 27000 | 2160 | 12.5 | 23200 | 2620 | 8.85 | 10.59 | Same as description | Same as description
97 | Split_Wall_Mounted LG 2.25TR SEER 10.49 | Split_Wall_Mounted | LG | ATNQ30GPLT4 | 27000 | 2180 | 12.39 | 24000 | 2760 | 8.7 | 10.49 | Same as description | Same as description
98 | Split_Wall_Mounted Carrier 2.25TR SEER 10.20 | Split_Wall_Mounted | Carrier | 42QTD024VS | 27000 | 2250 | 12 | 24000 | 2810 | 8.54 | 10.2 | Same as description | Same as description
99 | Split_Wall_Mounted Fuji 2.2TR SEER 8.66 | Split_Wall_Mounted | Fuji | RSA30FRTA-S | 27500 | 2700 | 10.19 | 24000 | 3290 | 7.29 | 8.66 | Same as description | Same as description
100 | Split_Ceiling_Cassette LG 2.31TR SEER 7.39 | Split_Ceiling_Cassette | LG | LTNC302PLEO | 27800 | 3240 | 8.58 | 24400 | 3800 | 6.42 | 7.39 | Same as description | Same as description
101 | Split_Ceiling_Cassette LG 2.32TR SEER 8.12 | Split_Ceiling_Cassette | LG | LTNC302NLE1 | 27807.7907 | 2920 | 9.52 | 24429.9119 | 3550 | 6.88 | 8.12 | Same as description | Same as description
102 | Split_Wall_Mounted LG 2.33TR SEER 10.46 | Split_Wall_Mounted | LG | T3224H / AS-W322V4B0 | 27978.3907 | 2320 | 12.06 | 24600.5118 | 2650 | 9.28 | 10.46 | Same as description | Same as description
103 | Split_Wall_Mounted LG 2.33TR SEER 10.54 | Split_Wall_Mounted | LG | T3224C / AS-Q322V4B0 | 27978.3907 | 2240 | 12.49 | 22382.7125 | 2510 | 8.92 | 10.54 | Same as description | Same as description
104 | Split_Wall_Mounted Samsung 2.33TR SEER 9.83 | Split_Wall_Mounted | Samsung | AR30JVFUCWKX | 28000 | 2430 | 11.52 | 25000 | 3010 | 8.31 | 9.83 | Same as description | Same as description
105 | Split_Wall_Mounted Zamil 2.35TR SEER 9.85 | Split_Wall_Mounted | Zamil | ADO30CHXCW | 28295.7066 | 2450 | 11.55 | 25296.5596 | 3048 | 8.3 | 9.85 | Same as description | Same as description
106 | Split_Wall_Mounted LG 2.5TR SEER 10.43 | Split_Wall_Mounted | LG | NT382H / S4-W32R43FA | 30000 | 2440 | 12.3 | 25400 | 2885 | 8.8 | 10.43 | Same as description | Same as description
107 | Split_Wall_Mounted Royal Temp 2.5TR SEER 7.53 | Split_Wall_Mounted | Royal Temp | MIS-300-HP | 30000 | 3448 | 8.7 | 24396 | 3587 | 6.8 | 7.53 | Same as description | Same as description
108 | Split_Wall_Mounted Carrier 2.58TR SEER 10.41 | Split_Wall_Mounted | Carrier | 42QHB030HS | 31000 | 2520 | 12.3 | 26500 | 3050 | 8.69 | 10.41 | Same as description | Same as description
109 | Split_Wall_Mounted LG 2.58TR SEER 9.72 | Split_Wall_Mounted | LG | T3624C / AS-Q362V4V0 | 31015.0697 | 2710 | 11.44 | 24805.2317 | 2960 | 8.38 | 9.72 | Same as description | Same as description
110 | Split_Wall_Mounted LG 2.58TR SEER 9.73 | Split_Wall_Mounted | LG | T3624H / AS-W362V4V0 | 31015.0697 | 2720 | 11.4 | 24771.1117 | 2920 | 8.48 | 9.73 | Same as description | Same as description
111 | Split_Wall_Mounted LG 2.6TR SEER 7.18 | Split_Wall_Mounted | LG | S382GH / LS-H382DSB0 | 31219.7896 | 3800 | 8.22 | 27466.5908 | 4220 | 6.51 | 7.18 | Same as description | Same as description
112 | Split_Wall_Mounted LG 2.62TR SEER 8.13 | Split_Wall_Mounted | LG | S3624H NV2 | 31390.3895 | 3300 | 9.51 | 28319.5906 | 4130 | 6.86 | 8.13 | Same as description | Same as description
113 | Split_Wall_Mounted Zamil 2.62TR SEER 10.00 | Split_Wall_Mounted | Zamil | ADO36CHXCW | 31499.5735 | 2669 | 11.8 | 27998.8627 | 3373 | 8.3 | 10 | Same as description | Same as description
114 | Split_Wall_Mounted Royal Temp 2.67TR SEER 7.44 | Split_Wall_Mounted | Royal Temp | MIS-320-HP | 32000 | 3720 | 8.6 | 26380 | 3937 | 6.7 | 7.44 | Same as description | Same as description
115 | Split_Wall_Mounted Carrier 2.75TR SEER 8.54 | Split_Wall_Mounted | Carrier | 38XP100H3PE/ 42XP100H3PE | 33000 | 3309.9298 | 9.97 | 29500 | 4057.7717 | 7.27 | 8.54 | Same as description | Same as description
116 | Split_Wall_Mounted Carrier 2.75TR SEER 8.81 | Split_Wall_Mounted | Carrier | 38XP100H3-E | 33000 | 3200 | 10.31 | 29500 | 3950 | 7.47 | 8.81 | Same as description | Same as description
117 | Split_Ceiling_Cassette Carrier 2.88TR SEER 10.05 | Split_Ceiling_Cassette | Carrier | 42KTD036HS | 34500 | 2950 | 11.69 | 31000 | 3600 | 8.61 | 10.05 | Same as description | Same as description
118 | Split_Floor_Standing LG 3.15TR SEER 7.86 | Split_Floor_Standing | LG | LP-C552TM3 | 37873.1874 | 4100 | 9.24 | 32072.7893 | 4800 | 6.68 | 7.86 | Same as description | Same as description
119 | Split_Floor_Standing Daewoo 3.16TR SEER 8.11 | Split_Floor_Standing | Daewoo | DPA-380RH / 300RH | 38000 | 4000 | 9.5 | 31500 | 4500 | 7 | 8.11 | Same as description | Same as description
120 | Split_Floor_Standing LG 3.32TR SEER 7.22 | Split_Floor_Standing | LG | LP-C552TE2 | 39920 | 4690 | 8.51 | 33096 | 5400 | 6.13 | 7.22 | Same as description | Same as description
121 | Split_Floor_Standing LG 3.33TR SEER 8.08 | Split_Floor_Standing | LG | LPNC452TM5 | 39988.6267 | 4200 | 9.52 | 34017.6287 | 4970 | 6.84 | 8.08 | Same as description | Same as description
122 | Split_Ceiling_Ducted LG 3.37TR SEER 7.02 | Split_Ceiling_Ducted | LG | LBNC422GSA4 | 40500.4265 | 5050 | 8.02 | 36508.3878 | 5750 | 6.35 | 7.02 | Same as description | Same as description
123 | Split_Floor_Standing Zamil 3.42TR SEER 6.87 | Split_Floor_Standing | Zamil | DFX48ESCNASQ | 40988.3423 | 5125 | 8 | 34491.8965 | 5725 | 6.02 | 6.87 | Same as description | Same as description
124 | Split_Floor_Standing Zamil 3.5TR SEER 8.37 | Split_Floor_Standing | Zamil | GFX48MTHNIV | 42000 | 4380 | 9.59 | 37530 | 5000 | 7.51 | 8.37 | Same as description | Same as description
125 | Split_Floor_Standing Carrier 3.54TR SEER 8.52 | Split_Floor_Standing | Carrier | 42SD6B.38HK48 | 42500 | 4336.7347 | 9.8 | 37000 | 4836.6013 | 7.65 | 8.52 | Same as description | Same as description
126 | Split_Floor_Standing Gree 3.62TR SEER 10.14 | Split_Floor_Standing | Gree | GVH48AH-D3NTA5A/O | 43500 | 3645 | 11.93 | 38200 | 4495 | 8.5 | 10.14 | Same as description | Same as description
127 | Split_Floor_Standing LG 3.72TR SEER 7.65 | Split_Floor_Standing | LG | LP-H552TM2 | 44697.1851 | 4930 | 9.07 | 37531.9875 | 5860 | 6.4 | 7.65 | Same as description | Same as description
128 | Split_Floor_Standing LG 3.75TR SEER 7.47 | Split_Floor_Standing | LG | LPNH552TM4 | 45038.385 | 5150 | 8.75 | 38896.787 | 6100 | 6.38 | 7.47 | Same as description | Same as description
129 | Split_Ceiling_Cassette LG 3.83TR SEER 9.87 | Split_Ceiling_Cassette | LG | ATUW48GMLT0SA0 | 45993.7447 | 3960 | 11.61 | 39067.387 | 4660 | 8.38 | 9.87 | Same as description | Same as description
130 | Split_Floor_Standing Zamil 3.83TR SEER 10.37 | Split_Floor_Standing | Zamil | MFZ48CSHDAD | 45997.1567 | 3740 | 12.3 | 40998.5783 | 4824 | 8.5 | 10.37 | Same as description | Same as description
131 | Split_Floor_Standing LG 3.84TR SEER 9.84 | Split_Floor_Standing | LG | APNQ50GT1M0 | 46096.1046 | 4000 | 11.52 | 39988.6267 | 4750 | 8.42 | 9.84 | Same as description | Same as description
132 | Split_Floor_Standing LG 3.84TR SEER 9.84 | Split_Floor_Standing | LG | APNQ50GT2E0 | 46096.1046 | 4000 | 11.52 | 39988.6267 | 4750 | 8.42 | 9.84 | Same as description | Same as description
133 | Split_Floor_Standing Samsung 4TR SEER 10.3 | Split_Floor_Standing | Samsung | AF55JV1MAEEX/ AF55JV1MAEEN | 48000 | 3930 | 12.21 | 42000 | 4950 | 8.48 | 10.3 | Same as description | Same as description
134 | Split_Floor_Standing LG 4TR SEER 10.51 | Split_Floor_Standing | LG | APNQ55GT3M2 | 48000 | 3870 | 12.4 | 43000 | 4940 | 8.7 | 10.51 | Same as description | Same as description
135 | Split_Floor_Standing LG 4TR SEER 10.51 | Split_Floor_Standing | LG | APNQ55GT3M4 | 48000 | 3870 | 12.4 | 43000 | 4940 | 8.7 | 10.51 | Same as description | Same as description
136 | Split_Floor_Standing Carrier 4TR SEER 9.95 | Split_Floor_Standing | Carrier | 42SDL6B | 48000 | 4100 | 11.71 | 41500 | 4950 | 8.38 | 9.95 | Same as description | Same as description
137 | Split_Floor_Standing LG 4.01TR SEER 7.95 | Split_Floor_Standing | LG | LPNC552TM4/TE3 | 48109 | 5200 | 9.25 | 42308 | 6150 | 6.88 | 7.95 | Same as description | Same as description
138 | Split_Floor_Standing LG 4.01TR SEER 8.67 | Split_Floor_Standing | LG | LPNC552T1M5/E5 | 48109.184 | 4750 | 10.13 | 42308.7859 | 5700 | 7.42 | 8.67 | Same as description | Same as description
139 | Split_Floor_Standing LG 4TR SEER 8.67 | Split_Floor_Standing | LG | LPNH552T1M5 | 48109.184 | 4750 | 10.13 | 42308.7859 | 5700 | 7.42 | 8.67 | Same as description | Same as description
140 | Split_Floor_Standing Samsung 4.16TR SEER 8.74 | Split_Floor_Standing | Samsung | APH553QF | 49967.442 | 5200 | 9.61 | 49967.442 | 5900 | 8.47 | 8.74 | Same as description | Same as description
141 | Split_Ceiling_Cassette LG 4.21TR SEER 7.69 | Split_Ceiling_Cassette | LG | LTUH602MLE0 | 50634.0631 | 5500 | 9.21 | 41967.586 | 6700 | 6.26 | 7.69 | Same as description | Same as description
142 | Split_Floor_Standing LG 4.35TR SEER 7.05 | Split_Floor_Standing | LG | LP-H652ME0 | 52203.5826 | 6190 | 8.43 | 42991.1857 | 7440 | 5.78 | 7.05 | Same as description | Same as description
143 | Split_Ceiling_Ducted Zamil 4.41TR SEER 9.83 | Split_Ceiling_Ducted | Zamil | KYA060H/DYA60H | 53000 | 4600 | 11.52 | 47200 | 5690 | 8.3 | 9.83 | Same as description | Same as description
144 | Split_Floor_Standing Zamil 4.421TR SEER 10.15 | Split_Floor_Standing | Zamil | MFZ60CSCDADC | 53056.5823 | 4416 | 12.01 | 45997.1567 | 5476 | 8.4 | 10.15 | Same as description | Same as description
145 | Split_Ceiling_Ducted Carrier 4.45TR SEER 8.30 | Split_Ceiling_Ducted | Carrier | 38MKS60US30-01 | 53500 | 5490 | 9.74 | 47000 | 6710 | 7 | 8.3 | Same as description | Same as description
146 | Split_Floor_Standing LG 4.49TR SEER 8.28 | Split_Floor_Standing | LG | LV-H602LLA3 | 53909.582 | 5600 | 9.63 | 47426.7842 | 6600 | 7.19 | 8.28 | Same as description | Same as description
147 | Split_Floor_Standing LG 4.5TR SEER 10.00 | Split_Floor_Standing | LG | ABUQ60LM3T0 / ABUQ54LM3T0 | 54000 | 4610 | 11.71 | 45600 | 5300 | 8.6 | 10 | Same as description | Same as description
148 | Split_Ceiling_Ducted LG 4.86TR SEER 7.90 | Split_Ceiling_Ducted | LG | LBNC602RSA4 | 58345.1806 | 6350 | 9.19 | 51214.1029 | 7500 | 6.83 | 7.9 | Same as description | Same as description
149 | Split_Wall_Mounted Daikin 1.78TR SEER 7.47 | Split_Wall_Mounted | Daikin | FTY24HEVLK | 21350 | 2470 | 8.64 | 18330 | 2770 | 6.62 | 7.47 | Same as description | Same as description
150 | Split_Wall_Mounted Daikin 2.28TR SEER 8.57 | Split_Wall_Mounted | Daikin | R30KEVLK / FT30KEVLK | 27300 | 2750 | 9.93 | 24000 | 3200 | 7.5 | 8.57 | Same as description | Same as description
151 | Split_Ceiling_Ducted YORK 1.5TR SEER 6.41 | Split_Ceiling_Ducted | YORK | YE3SD18OSHBW22-VH | 18000 | 2390 | 7.53 | 15480 | 2850 | 5.43 | 6.41 | Same as description | Same as description
152 | Split_Ceiling_Ducted YORK 2TR SEER 6.41 | Split_Ceiling_Ducted | YORK | YE3Cf24CS7AC22 | 24000 | 3190 | 7.52 | 20640 | 3800 | 5.43 | 6.41 | Same as description | Same as description
153 | Split_Ceiling_Ducted YORK 4TR SEER 6.90 | Split_Ceiling_Ducted | YORK | YE3SD48SECAC22-H | 48000 | 6380 | 7.52 | 41280 | 5570 | 7.41 | 6.9 | Same as description | Same as description
154 | Split_Ceiling_Ducted YORK 2.5TR SEER 6.40 | Split_Ceiling_Ducted | YORK | YE3SD30RSHAC22-H | 30000 | 3990 | 7.52 | 25800 | 4750 | 5.43 | 6.4 | Same as description | Same as description
155 | Split_Ceiling_Ducted YORK 3TR SEER 6.70 | Split_Ceiling_Ducted | YORK | YE3SD36RSHAD22-2 | 36000 | 4790 | 7.52 | 30960 | 4750 | 6.52 | 6.7 | Same as description | Same as description
156 | Split_Ceiling_Ducted YORK 5TR SEER 6.39 | Split_Ceiling_Ducted | YORK | YE3SD60SECBK22-H | 60000 | 7980 | 7.52 | 51600 | 9540 | 5.41 | 6.39 | Same as description | Same as description
157 | Window LG 1.39TR SEER 7.03 | Window | LG | W182EC SN2 /GWC182NAAB3 | 16719 | 2000 | 8.36 | 13477 | 2300 | 5.86 | 7.03 | Same as Description | Same as Description
158 | Window Carrier 1.43TR SEER 8.52 | Window | Carrier | 51HSR183MA0G | 17200 | 1720 | 10 | 15000 | 2083 | 7.2 | 8.52 | Same as Description | Same as Description
159 | Window Carrier 1.5TR SEER 8.62 | Window | Carrier | CRSR183M-0GSE | 17800 | 1745 | 10.2 | 15000 | 2083 | 7.2 | 8.62 | Same as Description | Same as Description
160 | Window LG 1.49TR SEER 7.24 | Window | LG | Z182EC | 17947 | 2110 | 8.51 | 15353 | 2500 | 6.14 | 7.24 | Same as Description | Same as Description
161 | Window Samsung 1.5TR SEER 6.82 | Window | Samsung | AHT18P1HBA | 18000 | 2200 | 8.18 | 14474 | 2600 | 5.57 | 6.82 | Same as Description | Same as Description
162 | Window LG 1.5TR SEER 7.70 | Window | LG | W182EH SN3 | 18000 | 2020 | 8.91 | 14978.675 | 2180 | 6.87 | 7.7 | Same as Description | Same as Description
163 | Window LG 1.5TR SEER 7.70 | Window | LG | LWH182NFAZ3 | 18000 | 2020 | 8.91 | 14978.675 | 2180 | 6.87 | 7.7 | Same as Description | Same as Description
164 | Window Zamil 1.5TR SEER 6.80 | Window | Zamil | YHB18CTEYIINW | 18000 | 2200 | 8.18 | 14000 | 2520 | 5.56 | 6.8 | Same as Description | Same as Description
165 | Window Zamil 1.5TR SEER 6.51 | Window | Zamil | PCB19CKXQIMNW | 18260 | 2360 | 7.74 | 14260 | 2600 | 5.48 | 6.51 | Same as Description | Same as Description
166 | Window Zamil 1.5TR SEER 6.80 | Window | Zamil | ACB19CTXPIMNW | 18500 | 2260 | 8.19 | 14000 | 2510 | 5.58 | 6.8 | Same as Description | Same as Description
167 | Window Zamil 1.5TR SEER 6.92 | Window | Zamil | AHB19CTEPIMNW | 18500 | 2220 | 8.33 | 14500 | 2580 | 5.62 | 6.92 | Same as Description | Same as Description
168 | Window LG 1.74TR SEER 7.22 | Window | LG | W242EH SN0 | 20983.793 | 2500 | 8.39 | 18493.0338 | 2950 | 6.27 | 7.22 | Same as Description | Same as Description
169 | Window York 1.75TR SEER 8.45 | Window | York | NYSR243M-0G8 | 21000 | 2100 | 10 | 17500 | 2465 | 7.1 | 8.45 | Same as Description | Same as Description
170 | Window Zamil 1.79TR SEER 6.38 | Window | Zamil | ZHB24CPEQIMNW | 21500 | 2870 | 7.49 | 18000 | 3300 | 5.45 | 6.38 | Same as Description | Same as Description
171 | Window Zamil 1.88TR SEER 7.28 | Window | Zamil | NHB24CGERIMNW | 22500 | 2630 | 8.56 | 19500 | 3170 | 6.15 | 7.28 | Same as Description | Same as Description
172 | Window LG 2TR SEER 7.48 | Window | LG | W242EH | 24000 | 2560 | 9.38 | 16206 | 2880 | 5.63 | 7.48 | Same as Description | Same as Description
173 | Window Zamil 2TR SEER 6.34 | Window | Zamil | PHB24CIEQIINW | 24000 | 3200 | 7.5 | 19000 | 3520 | 5.4 | 6.34 | Same as Description | Same as Description
174 | Window Royal Temp 2TR SEER 6.41 | Window | Royal Temp | WGS-24PE | 24000 | 3190 | 7.52 | 20640 | 3800 | 5.43 | 6.41 | Same as Description | Same as Description
175 | Window Zamil 2TR SEER 6.23 | Window | Zamil | AHB26CHHLKKNW | 24000 | 3330 | 7.21 | 18800 | 3300 | 5.7 | 6.23 | Same as Description | Same as Description
176 | Window Zamil 2TR SEER 6.41 | Window | Zamil | ACB24CIXPIMNW | 24000 | 3100 | 7.74 | 18000 | 3450 | 5.22 | 6.41 | Same as Description | Same as Description
177 | Window Zamil 2TR SEER 6.95 | Window | Zamil | LCB24CTXCIING | 24000 | 2800 | 8.57 | 18000 | 3350 | 5.37 | 6.95 | Same as Description | Same as Description
178 | Window Zamil 2TR SEER 7.22 | Window | Zamil | AHB24CMESAANW | 24000 | 2750 | 8.73 | 18000 | 3060 | 5.88 | 7.22 | Same as Description | Same as Description
179 | Window Zamil 2TR SEER 7.33 | Window | Zamil | AHB26CRELIINW | 24000 | 2710 | 8.86 | 17900 | 3001 | 5.96 | 7.33 | Same as Description | Same as Description
180 | Window Zamil 2TR SEER 7.10 | Window | Zamil | AHB24CREPLNW | 24000 | 2800 | 8.57 | 18000 | 3100 | 5.81 | 7.1 | Same as Description | Same as Description
181 | Window Zamil 2TR SEER 7.20 | Window | Zamil | AHB25CEBW | 24000 | 2750 | 8.73 | 18000 | 3100 | 5.81 | 7.2 | Same as Description | Same as Description
182 | Window Zamil 2TR SEER 6.95 | Window | Zamil | UHB25CTESIJNW | 24000 | 2800 | 8.57 | 18000 | 3350 | 5.37 | 6.95 | Same as Description | Same as Description
183 | Window Zamil 2TR SEER 7.24 | Window | Zamil | CHB24CEDW | 24000 | 2750 | 8.73 | 18000 | 3020 | 5.96 | 7.24 | Same as Description | Same as Description
184 | Window York 2TR SEER 7.22 | Window | York | LYSD243M-0B5 / NYSD243M-0B5 | 24050 | 2813 | 8.55 | 18970 | 3089 | 6.14 | 7.22 | Same as Description | Same as Description
185 | Window Zamil 2TR SEER 7.22 | Window | Zamil | HHB24CHERKINW | 24050 | 2813 | 8.55 | 19000 | 3104 | 6.12 | 7.22 | Same as Description | Same as Description
186 | Window Zamil Classic 2TR SEER 7.22 | Window | Zamil | AHB26CHERKINW | 24050 | 2813 | 8.55 | 19000 | 3104 | 6.12 | 7.22 | Same as Description | Same as Description
187 | Window Zamil 2.01TR SEER 7.86 | Window | Zamil | LCB24CKXGKINW | 24196 | 2574 | 9.4 | 19000 | 2920 | 6.51 | 7.86 | Same as Description | Same as Description
188 | Window York 2.01TR SEER 7.57 | Window | York | LYSD243M-0C8 / NYSD243M-0C8 | 24200 | 2674 | 9.05 | 18700 | 2968 | 6.3 | 7.57 | Same as Description | Same as Description
189 | Window Carrier 2.01TR SEER 7.57 | Window | Carrier | CRSD243M-0C8 | 24200 | 2674 | 9.05 | 18700 | 2968 | 6.3 | 7.57 | Same as Description | Same as Description
190 | Window Carrier 2.01TR SEER 7.59 | Window | Carrier | C2K24MB-RG9 | 24200 | 2674 | 9.05 | 19500 | 3095 | 6.3 | 7.59 | Same as Description | Same as Description
191 | Window HAAS 2.01TR SEER 7.93 | Window | HAAS | HE24E6YH3XHS00 | 24200 | 2574 | 9.4 | 21000 | 3206 | 6.55 | 7.93 | Same as Description | Same as Description
192 | Window Zamil 2.01TR SEER 7.86 | Window | Zamil | HHB24CKEGKINW | 24200 | 2574 | 9.4 | 19000 | 2920 | 6.51 | 7.86 | Same as Description | Same as Description
193 | Window Zamil 2.01TR SEER 7.89 | Window | Zamil | ZHD24CAEGKNNW | 24200 | 2574 | 9.4 | 20000 | 3075 | 6.5 | 7.89 | Same as Description | Same as Description
194 | Window Carrier 2.02TR SEER 7.57 | Window | Carrier | 51HSD243MA0C | 24200 | 2674 | 9.05 | 18700 | 2968 | 6.3 | 7.57 | Same as Description | Same as Description
195
196
197
198
199
200
201
202
203
204
205
206
207
208
209
210
211
212
213
214
215
216
217
218
219
220
221
222
223
224
225
226
227
228
229
230
231
232
233
234
235
236
237
238
239
240
241
242
243
244
245
246
247
248
249
250
251
252
253
254
255
256
257
258
259
260
261
262
263
264
265
266
267
268
269
270
271
272
273
274
275
276
277
278
279
280
281
282
283
284
285
286
287
288
289
290
291
292
293
294
295
296
297
298
299
300

## Old_Model_Registry
S.N | Equipment_Type | Make | Model No (ID/ OD) | Compressor Type | Size Category | TR | T1 (Btu/h) | T1 (W) | T1 EER (Btu/h /W) | T3 (Btu/h) | T3 (W) | T3 EER (Btu/h /W) | Equivalent SEER | Surveyed Unit Description | Equivalent AC Model Description
1 | Window | LG | B182C | Non-Inverter | 2 | 2 | 24000 | 2500 | 9.6 | 21000 | 3000 | 7 | 8.21 | Window LG 2TR SEER 8.21 | Window LG 2TR SEER 7.48
2 | Window | Carrier | CRVR243M-0G8 | Non-Inverter | 2 | 1.75 | 21000 | 2100 | 10 | 17500 | 2465 | 7.0994 | 8.46 | Window Carrier 1.75TR SEER 8.46 | Window York 1.75TR SEER 8.45
3 | Window | Carrier | CRVR243M-0G5 | Non-Inverter | 2 | 2 | 24050 | 2812 | 8.5526 | 20500 | 3333 | 6.1506 | 7.27 | Window Carrier 2TR SEER 7.27 | Window Zamil 2TR SEER 7.24
4 | Window | Carrier | CRSR183M-008 | Non-Inverter | 1.5 | 1.43 | 17200 | 1720 | 10 | 15000 | 2083 | 7.2012 | 8.52 | Window Carrier 1.43TR SEER 8.52 | Window Carrier 1.43TR SEER 8.52
5 | Window | Zamil | PAB24CIEQIN | Non-Inverter | 2 | 2 | 24000 | 3200 | 7.5 | 19000 | 3520 | 5.3977 | 6.34 | Window Zamil 2TR SEER 6.34 | Window Zamil 2TR SEER 6.34
6 | Window | Haas | H0125E8Y | Non-Inverter | 2 | 1.83 | 22000 | 2155 | 10.2088 | 18500 | 2570 | 7.1984 | 8.63 | Window Haas 1.83TR SEER 8.63 | Window York 1.75TR SEER 8.45
7 | Window | Falcon | FSVR243M | Non-Inverter | 2 | 1.75 | 21000 | 2100 | 10 | 17500 | 2465 | 7.0994 | 8.46 | Window Falcon 1.75TR SEER 8.46 | Window York 1.75TR SEER 8.45
8 | Window | Zamil | HHB19CHETI | Non-Inverter | 1.5 | 1.5 | 18050 | 1857 | 9.72 | 14500 | 2077 | 6.9812 | 8.23 | Window Zamil 1.5TR SEER 8.23 | Window Carrier 1.43TR SEER 8.52
9 | Window | Carrier | CRVR243M-oM | Non-Inverter | 2 | 2 | 24000 | 2700 | 8.8889 | 18493 | 3100 | 5.9655 | 7.37 | Window Carrier 2TR SEER 7.37 | Window Zamil 2TR SEER 7.33
10 | Window | Zamil | ZHB18CGERIMNW | Non-Inverter | 1.5 | 1.45 | 17500 | 2050 | 8.5366 | 16000 | 2440 | 6.5574 | 7.43 | Window Zamil 1.45TR SEER 7.43 | Window LG 1.5TR SEER 7.70
11 | Window | Midea | MWTF2 | Non-Inverter | 2 | 1.7 | 20400 | 2042 | 9.9902 | 17400 | 2429 | 7.1634 | 8.49 | Window Midea 1.7TR SEER 8.49 | Window York 1.75TR SEER 8.45
12 | Window | TIT | T2-24Ht16 | Non-Inverter | 2 | 1.69 | 20300 | 2055 | 9.8783 | 17300 | 2440 | 7.0902 | 8.4 | Window TIT 1.69TR SEER 8.4 | Window York 1.75TR SEER 8.45
13 | Window | LG | W182EC SN2 /GWC182NAAB3 | Non-Inverter | 1.5 | 1.39 | 16719 | 2000 | 8.3595 | 13477 | 2300 | 5.8596 | 7.03 | Window LG 1.39TR SEER 7.03 | Window LG 1.39TR SEER 7.03
14 | Window | Carrier | 51HSR183MA0G | Non-Inverter | 1.5 | 1.43 | 17200 | 1720 | 10 | 15000 | 2083 | 7.2012 | 8.52 | Window Carrier 1.43TR SEER 8.52 | Window Carrier 1.43TR SEER 8.52
15 | Window | Carrier | CRSR183M-0GSE | Non-Inverter | 1.5 | 1.48 | 17800 | 1745 | 10.2006 | 15000 | 2083 | 7.2012 | 8.62 | Window Carrier 1.48TR SEER 8.62 | Window Carrier 1.5TR SEER 8.62
16 | Window | LG | Z182EC | Non-Inverter | 1.5 | 1.49 | 17947 | 2110 | 8.5057 | 15353 | 2500 | 6.1412 | 7.24 | Window LG 1.49TR SEER 7.24 | Window LG 1.49TR SEER 7.24
17 | Window | Samsung | AHT18P1HBA | Non-Inverter | 1.5 | 1.5 | 18000 | 2200 | 8.1818 | 14474 | 2600 | 5.5669 | 6.83 | Window Samsung 1.5TR SEER 6.83 | Window Samsung 1.5TR SEER 6.82
18 | Window | LG | W182EH SN3 | Non-Inverter | 1.5 | 1.5 | 18000 | 2020 | 8.9109 | 14978.675 | 2180 | 6.871 | 7.7 | Window LG 1.5TR SEER 7.7 | Window LG 1.5TR SEER 7.70
19 | Window | LG | LWH182NFAZ3 | Non-Inverter | 1.5 | 1.5 | 18000 | 2020 | 8.9109 | 14978.675 | 2180 | 6.871 | 7.7 | Window LG 1.5TR SEER 7.7 | Window LG 1.5TR SEER 7.70
20 | Window | Zamil | YHB18CTEYIINW | Non-Inverter | 1.5 | 1.5 | 18000 | 2200 | 8.1818 | 14000 | 2520 | 5.5556 | 6.81 | Window Zamil 1.5TR SEER 6.81 | Window Zamil 1.5TR SEER 6.80
21 | Window | Zamil | ACB19CTXPIMNW | Non-Inverter | 1.5 | 1.54 | 18500 | 2260 | 8.1858 | 14000 | 2510 | 5.5777 | 6.8 | Window Zamil 1.54TR SEER 6.8 | Window Carrier 1.43TR SEER 8.52
22 | Window | Zamil | AHB19CTEPIMNW | Non-Inverter | 1.5 | 1.54 | 18500 | 2220 | 8.3333 | 14500 | 2580 | 5.6202 | 6.92 | Window Zamil 1.54TR SEER 6.92 | Window Carrier 1.43TR SEER 8.52
23 | Window | LG | W242EH SN0 | Non-Inverter | 2 | 1.74 | 20983.793 | 2500 | 8.3935 | 18493.0338 | 2950 | 6.2688 | 7.23 | Window LG 1.74TR SEER 7.23 | Window LG 1.74TR SEER 7.22
24 | Window | York | NYSR243M-0G8 | Non-Inverter | 2 | 1.75 | 21000 | 2100 | 10 | 17500 | 2465 | 7.0994 | 8.46 | Window York 1.75TR SEER 8.46 | Window York 1.75TR SEER 8.45
25 | Window | Zamil | NHB24CGERIMNW | Non-Inverter | 2 | 1.87 | 22500 | 2630 | 8.5551 | 19500 | 3170 | 6.1514 | 7.28 | Window Zamil 1.87TR SEER 7.28 | Window Zamil 1.88TR SEER 7.28
26 | Window | LG | W242EH | Non-Inverter | 2 | 2 | 24000 | 2560 | 9.375 | 16206 | 2880 | 5.6271 | 7.48 | Window LG 2TR SEER 7.48 | Window LG 2TR SEER 7.48
27 | Window | Zamil | PHB24CIEQIINW | Non-Inverter | 2 | 2 | 24000 | 3200 | 7.5 | 19000 | 3520 | 5.3977 | 6.34 | Window Zamil 2TR SEER 6.34 | Window Zamil 2TR SEER 6.34
28 | Window | Royal_Temp | WGS-24PE | Non-Inverter | 2 | 2 | 24000 | 3190 | 7.5235 | 20640 | 3800 | 5.4316 | 6.41 | Window Royal_Temp 2TR SEER 6.41 | Window Royal Temp 2TR SEER 6.41
29 | Window | Zamil | AHB26CHHLKKNW | Non-Inverter | 2 | 2 | 24000 | 3330 | 7.2072 | 18800 | 3300 | 5.697 | 6.24 | Window Zamil 2TR SEER 6.24 | Window Zamil 2TR SEER 6.23
30 | Window | Zamil | ACB24CIXPIMNW | Non-Inverter | 2 | 2 | 24000 | 3100 | 7.7419 | 18000 | 3450 | 5.2174 | 6.41 | Window Zamil 2TR SEER 6.41 | Window Royal Temp 2TR SEER 6.41
31 | Window | Zamil | LCB24CTXCIING | Non-Inverter | 2 | 2 | 24000 | 2800 | 8.5714 | 18000 | 3350 | 5.3731 | 6.96 | Window Zamil 2TR SEER 6.96 | Window Zamil 2TR SEER 6.95
32 | Window | Zamil | AHB24CMESAANW | Non-Inverter | 2 | 2 | 24000 | 2750 | 8.7273 | 18000 | 3060 | 5.8824 | 7.23 | Window Zamil 2TR SEER 7.23 | Window Zamil 2TR SEER 7.22
33 | Window | Zamil | AHB26CRELIINW | Non-Inverter | 2 | 2 | 24000 | 2710 | 8.8561 | 17900 | 3001 | 5.9647 | 7.33 | Window Zamil 2TR SEER 7.33 | Window Zamil 2TR SEER 7.33
34 | Window | Zamil | AHB24CREPLNW | Non-Inverter | 2 | 2 | 24000 | 2800 | 8.5714 | 18000 | 3100 | 5.8065 | 7.11 | Window Zamil 2TR SEER 7.11 | Window Zamil 2TR SEER 7.10
35 | Window | Zamil | AHB25CEBW | Non-Inverter | 2 | 2 | 24000 | 2750 | 8.7273 | 18000 | 3100 | 5.8065 | 7.2 | Window Zamil 2TR SEER 7.2 | Window Zamil 2TR SEER 7.20
36 | Window | Zamil | UHB25CTESIJNW | Non-Inverter | 2 | 2 | 24000 | 2800 | 8.5714 | 18000 | 3350 | 5.3731 | 6.96 | Window Zamil 2TR SEER 6.96 | Window Zamil 2TR SEER 6.95
37 | Window | Zamil | CHB24CEDW | Non-Inverter | 2 | 2 | 24000 | 2750 | 8.7273 | 18000 | 3020 | 5.9603 | 7.25 | Window Zamil 2TR SEER 7.25 | Window Zamil 2TR SEER 7.24
38 | Window | York | LYSD243M-0B5 / NYSD243M-0B5 | Non-Inverter | 2 | 2 | 24050 | 2813 | 8.5496 | 18970 | 3089 | 6.1411 | 7.23 | Window York 2TR SEER 7.23 | Window Zamil 2TR SEER 7.24
39 | Window | Zamil | HHB24CHERKINW | Non-Inverter | 2 | 2 | 24050 | 2813 | 8.5496 | 19000 | 3104 | 6.1211 | 7.22 | Window Zamil 2TR SEER 7.22 | Window Zamil 2TR SEER 7.22
40 | Window | Zamil | AHB26CHERKINW | Non-Inverter | 2 | 2 | 24050 | 2813 | 8.5496 | 19000 | 3104 | 6.1211 | 7.22 | Window Zamil 2TR SEER 7.22 | Window Zamil 2TR SEER 7.22
41 | Window | Zamil | LCB24CKXGKINW | Non-Inverter | 2 | 2.01 | 24196 | 2574 | 9.4002 | 19000 | 2920 | 6.5068 | 7.87 | Window Zamil 2.01TR SEER 7.87 | Window Zamil 2.01TR SEER 7.86
42 | Window | York | LYSD243M-0C8 / NYSD243M-0C8 | Non-Inverter | 2 | 2.01 | 24200 | 2674 | 9.0501 | 18700 | 2968 | 6.3005 | 7.58 | Window York 2.01TR SEER 7.58 | Window York 2.01TR SEER 7.57
43 | Window | Carrier | CRSD243M-0C8 | Non-Inverter | 2 | 2.01 | 24200 | 2674 | 9.0501 | 18700 | 2968 | 6.3005 | 7.58 | Window Carrier 2.01TR SEER 7.58 | Window York 2.01TR SEER 7.57
44 | Window | Carrier | C2K24MB-RG9 | Non-Inverter | 2 | 2.01 | 24200 | 2674 | 9.0501 | 19500 | 3095 | 6.3005 | 7.6 | Window Carrier 2.01TR SEER 7.6 | Window Carrier 2.01TR SEER 7.59
45 | Window | Haas | HE24E6YH3XHS00 | Non-Inverter | 2 | 2.01 | 24200 | 2574 | 9.4017 | 21000 | 3206 | 6.5502 | 7.94 | Window Haas 2.01TR SEER 7.94 | Window HAAS 2.01TR SEER 7.93
46 | Window | Zamil | HHB24CKEGKINW | Non-Inverter | 2 | 2.01 | 24200 | 2574 | 9.4017 | 19000 | 2920 | 6.5068 | 7.87 | Window Zamil 2.01TR SEER 7.87 | Window Zamil 2.01TR SEER 7.86
47 | Window | Zamil | ZHD24CAEGKNNW | Non-Inverter | 2 | 2.01 | 24200 | 2574 | 9.4017 | 20000 | 3075 | 6.5041 | 7.89 | Window Zamil 2.01TR SEER 7.89 | Window Zamil 2.01TR SEER 7.89
48 | Window | Carrier | 51HSD243MA0C | Non-Inverter | 2 | 2.01 | 24200 | 2674 | 9.0501 | 18700 | 2968 | 6.3005 | 7.58 | Window Carrier 2.01TR SEER 7.58 | Window York 2.01TR SEER 7.57
49 | Window | Frego | FT18X2P22 | Non-Inverter | 1.5 | 1.45 | 17500 | 1750 | 10 | 15000 | 2098 | 7.1497 | 8.49 | Window Frego 1.45TR SEER 8.49 | Window Carrier 1.43TR SEER 8.52
50 | Window | Carrier | CRSD183M-0C | Non-Inverter | 1.5 | 1.5 | 18000 | 2300 | 7.8261 | 14504 | 2650 | 5.4732 | 6.58 | Window Carrier 1.5TR SEER 6.58 | Window Zamil 1.5TR SEER 6.51
51 | Window | Frego | FT18X-2A5 | Non-Inverter | 1.5 | 1.51 | 18200 | 1850 | 9.8378 | 15390 | 2160 | 7.125 | 8.38 | Window Frego 1.51TR SEER 8.38 | Window Carrier 1.43TR SEER 8.52
52 | Window | Carrier | 51HVR213MAOG | Non-Inverter | 2 | 1.75 | 21000 | 2100 | 10 | 17500 | 2465 | 7.0994 | 8.46 | Window Carrier 1.75TR SEER 8.46 | Window York 1.75TR SEER 8.45
53 | Window | Carrier | CRSR243M-OG8 | Non-Inverter | 2 | 1.75 | 21000 | 2100 | 10 | 17500 | 2465 | 7.0994 | 8.46 | Window Carrier 1.75TR SEER 8.46 | Window York 1.75TR SEER 8.45
54 | Window | York | YE7WL24EC841-0 | Non-Inverter | 2 | 1.83 | 22000 | 2172 | 10.1289 | 17750 | 2515 | 7.0577 | 8.51 | Window York 1.83TR SEER 8.51 | Window York 1.75TR SEER 8.45
55 | Window | Classic | PCB24CIXQIINW | Non-Inverter | 2 | 2 | 24000 | 3200 | 7.5 | 19000 | 3520 | 5.3977 | 6.34 | Window Classic 2TR SEER 6.34 | Window Zamil 2TR SEER 6.34
56 | Window | Zamil | ZHB24CGERKINW2 | Non-Inverter | 2 | 2 | 24050 | 2807 | 8.5679 | 20000 | 3267 | 6.1218 | 7.26 | Window Zamil 2TR SEER 7.26 | Window Zamil 2TR SEER 7.24
57 | Window | Carrier | 51HVD243MAOC | Non-Inverter | 2 | 2.01 | 24200 | 2674 | 9.0501 | 18700 | 2968 | 6.3005 | 7.58 | Window Carrier 2.01TR SEER 7.58 | Window York 2.01TR SEER 7.57
58 | Window | LG | W242EC | Non-Inverter | 2 | 2 | 24000 | 2440 | 9.8361 | 16719 | 2900 | 5.7652 | 7.81 | Window LG 2TR SEER 7.81 | Window LG 2TR SEER 7.48
59 | Window | York | AR24HCFNBWKN | Non-Inverter | 2 | 1.93 | 23200 | 2340 | 9.9145 | 20230 | 2700 | 7.4926 | 8.56 | Window York 1.93TR SEER 8.56 | Window York 1.75TR SEER 8.45
60 | Window | LG | W242EHSN0 | Non-Inverter | 2 | 1.74 | 20985 | 2500 | 8.394 | 18493 | 2950 | 6.2688 | 7.23 | Window LG 1.74TR SEER 7.23 | Window LG 1.74TR SEER 7.22
61 | Window | Hotpoint | KRJ24BBS1 | Non-Inverter | 2 | 1.8 | 21717 | 2750 | 7.8971 |  |  |  |  | Window Hotpoint 1.8TR SEER | Window York 1.75TR SEER 8.45
62 | Window | York | NYSD243M-0B3 | Non-Inverter | 2 | 1.83 | 22000 | 2530 | 8.6957 | 17504 | 2820 | 6.2071 | 7.34 | Window York 1.83TR SEER 7.34 | Window Zamil 2TR SEER 7.33
63 | Window | Carrier | CRVD243M-0C | Non-Inverter | 2 | 1.83 | 22000 | 2600 | 8.4615 | 17514 | 2800 | 6.255 | 7.21 | Window Carrier 1.83TR SEER 7.21 | Window LG 1.74TR SEER 7.22
64 | Window | Gree | GJC24AE-D3MTD5A | Non-Inverter | 2 | 1.82 | 21850 | 2150 | 10.1628 | 18300 | 2550 | 7.1765 | 8.59 | Window Gree 1.82TR SEER 8.59 | Window York 1.75TR SEER 8.45
65 | Window | Carrier | CRSD183M-0B-5 | Non-Inverter | 1.5 | 1.54 | 18500 | 1897 | 9.7522 | 15000 | 2143 | 6.9995 | 8.26 | Window Carrier 1.54TR SEER 8.26 | Window Carrier 1.43TR SEER 8.52
66 | Window | Gree | GJC18AE-D3NMTB4B | Non-Inverter | 1.5 | 1.61 | 19400 | 1960 | 9.898 | 15800 | 2200 | 7.1818 | 8.41 | Window Gree 1.61TR SEER 8.41 | Window York 1.75TR SEER 8.45
67 | Window | LG | W182BC | Non-Inverter | 1.5 | 1.5 | 18000 | 2090 | 8.6124 | 15000 | 2240 | 6.6964 | 7.46 | Window LG 1.5TR SEER 7.46 | Window LG 1.5TR SEER 7.70
68 | Window | General | ANJ18BDS1D | Non-Inverter | 1.5 | 1.5 | 18000 | 2100 | 8.5714 |  |  |  |  | Window General 1.5TR SEER | Window Carrier 1.5TR SEER 8.62
69 | Window | York | Nysd183m | Non-Inverter | 1.5 | 1.54 | 18500 | 1897 | 9.7522 | 15013.46 | 2143 | 7.0058 | 8.26 | Window York 1.54TR SEER 8.26 | Window Carrier 1.43TR SEER 8.52
70 | Window | AlESSA | DO24E8H3J | Non-Inverter | 2 | 1.78 | 21458 | 2490 | 8.6177 | 16822 | 2740 | 6.1394 | 7.26 | Window AlESSA 1.78TR SEER 7.26 | Window Zamil 1.88TR SEER 7.28
71 | Window | Falcon | FCWH 24 | Non-Inverter | 2 | 2 | 24000 | 2970 | 8.0808 |  |  |  |  | Window Falcon 2TR SEER | Window LG 2TR SEER 7.48
72 | Window | York | NYVR243M-0G5 | Non-Inverter | 2 | 2 | 24050 | 2813 | 8.5496 | 20472 | 3333 | 6.1422 | 7.27 | Window York 2TR SEER 7.27 | Window Zamil 2TR SEER 7.24
73 | Window | Zamil | ZHB24CGERIMNW | Non-Inverter | 2 | 1.87 | 22500 | 2630 | 8.5551 | 19500 | 3170 | 6.1514 | 7.28 | Window Zamil 1.87TR SEER 7.28 | Window Zamil 1.88TR SEER 7.28
74 | Window | Gree | GJC24AE-D3NMTG1D | Non-Inverter | 2 | 1.81 | 21800 | 2150 | 10.1395 | 18300 | 2550 | 7.1765 | 8.58 | Window Gree 1.81TR SEER 8.58 | Window York 1.75TR SEER 8.45
75 | Window | Mando | AC-24H-WND-MD | Non-Inverter | 2 | 1.7 | 20400 | 2042 | 9.9902 | 17400 | 2429 | 7.1634 | 8.49 | Window Mando 1.7TR SEER 8.49 | Window York 1.75TR SEER 8.45
76 | Window | QUEEN | HQWG24H | Non-Inverter | 2 | 1.76 | 21175 | 2750 | 7.7 | 17750 | 3200 | 5.5469 | 6.54 | Window QUEEN 1.76TR SEER 6.54 | Window Zamil 1.79TR SEER 6.38
77 | Window | Falcon | FSVR243M-0G8 | Non-Inverter | 2 | 1.75 | 21000 | 2100 | 10 | 17500 | 2465 | 7.0994 | 8.46 | Window Falcon 1.75TR SEER 8.46 | Window York 1.75TR SEER 8.45
78 | Window | Haas | HWA24Y6M | Non-Inverter | 2 | 1.73 | 20800 | 2087 | 9.9665 | 17700 | 2463 | 7.1864 | 8.48 | Window Haas 1.73TR SEER 8.48 | Window York 1.75TR SEER 8.45
79 | Window | ARROW | RO-24WHMG | Non-Inverter | 2 | 1.73 | 20800 | 2040 | 10.1961 | 17700 | 2424 | 7.302 | 8.66 | Window ARROW 1.73TR SEER 8.66 | Window York 1.75TR SEER 8.45
80 | Window | LG | Z242EH | Non-Inverter | 2 | 1.67 | 20131 | 2365 | 8.5121 | 17231 | 2810 | 6.132 | 7.24 | Window LG 1.67TR SEER 7.24 | Window LG 1.74TR SEER 7.22
81 | Window | Zamil | SHB18CREYIINW | Non-Inverter | 1.5 | 1.5 | 18000 | 2200 | 8.1818 | 12600 | 2300 | 5.4783 | 6.74 | Window Zamil 1.5TR SEER 6.74 | Window Zamil 1.5TR SEER 6.80
82 | Window | Zamil | UHB20CTESIINW | Non-Inverter | 1.5 | 1.58 | 19000 | 2100 | 9.0476 | 14500 | 2400 | 6.0417 | 7.48 | Window Zamil 1.58TR SEER 7.48 | Window LG 1.5TR SEER 7.70
83 | Window | LG | Z182EH | Non-Inverter | 1.5 | 1.49 | 17948 | 2110 | 8.5062 | 15116 | 2460 | 6.1447 | 7.24 | Window LG 1.49TR SEER 7.24 | Window LG 1.49TR SEER 7.24
84 | Window | AlESSA | H019E8H3Y | Non-Inverter | 1.5 | 1.43 | 17265 | 1960 | 8.8087 | 14331 | 2340 | 6.1244 | 7.41 | Window AlESSA 1.43TR SEER 7.41 | Window LG 1.49TR SEER 7.24
85 | Split_Wall_Mounted | LG | S122SH / GS-H122E0B1 | Non-Inverter | 1 | 0.95 | 11498.4362 | 1200 | 9.582 | 10235.9966 | 1400 | 7.3114 | 8.31 | Split_Wall_Mounted LG 0.95TR SEER 8.31 | Split_Wall_Mounted LG 0.95TR SEER 8.3
86 | Split_Wall_Mounted | Carrier | 42QHF012H | Non-Inverter | 1 | 0.95 | 11500 | 940 | 12.234 | 9700 | 1110 | 8.7387 | 10.37 | Split_Wall_Mounted Carrier 0.95TR SEER 10.37 | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
87 | Split_Wall_Mounted | Chigo | CZS-18CH | Non-Inverter | 1.5 | 1.38 | 16675 | 1450 | 11.5 | 14362 | 1670 | 8.6 | 9.89 | Split_Wall_Mounted Chigo 1.38TR SEER 9.89 | Split_Wall_Mounted Chigo 1.38TR SEER 9.88
88 | Split_Wall_Mounted | York | YE6HC18SH/YE6SD180SHZW41 | Non-Inverter | 1.5 | 1.42 | 17040 | 1478 | 11.5291 | 15097 | 1819 | 8.2996 | 9.84 | Split_Wall_Mounted York 1.42TR SEER 9.84 | Split_Wall_Mounted York 1.42TR SEER 9.83
89 | Split_Wall_Mounted | LG | B1828H N51 | Non-Inverter | 1.5 | 1.45 | 17469.4342 | 1510 | 11.5692 | 14978.675 | 1800 | 8.3215 | 9.84 | Split_Wall_Mounted LG 1.45TR SEER 9.84 | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
90 | Split_Wall_Mounted | LG | S182DC u51 | Non-Inverter | 1.5 | 1.45 | 17500 | 2000 | 8.75 | 15300 | 2300 | 6.6522 | 7.57 | Split_Wall_Mounted LG 1.45TR SEER 7.57 | Split_Wall_Mounted LG 1.46TR SEER 7.56
91 | Split_Wall_Mounted | LG | S182SC / LSUC1825SB0 | Non-Inverter | 1.5 | 1.45 | 17503 | 2050 | 8.538 | 15183 | 2450 | 6.1971 | 7.29 | Split_Wall_Mounted LG 1.45TR SEER 7.29 | Split_Wall_Mounted LG 1.46TR SEER 7.28
92 | Split_Wall_Mounted | LG | S182DC N51 | Non-Inverter | 1.5 | 1.45 | 17503.5542 | 2000 | 8.7518 | 15353.9949 | 2300 | 6.6756 | 7.58 | Split_Wall_Mounted LG 1.45TR SEER 7.58 | Split_Wall_Mounted LG 1.46TR SEER 7.57
93 | Split_Wall_Mounted | LG | A1828P nco | Non-Inverter | 1.5 | 1.45 | 17503.5542 | 1520 | 11.5155 | 15012.795 | 1810 | 8.2944 | 9.8 | Split_Wall_Mounted LG 1.45TR SEER 9.8 | Split_Wall_Mounted LG 1.46TR SEER 9.8
94 | Split_Wall_Mounted | LG | T182NC NC0 / LS Q182CNC0 | Non-Inverter | 1.5 | 1.47 | 17742 | 1500 | 11.828 | 15286 | 1740 | 8.7851 | 10.15 | Split_Wall_Mounted LG 1.47TR SEER 10.15 | Split_Wall_Mounted LG 1.47TR SEER 10.15
95 | Split_Wall_Mounted | Ugine | UASG18H | Non-Inverter | 1.5 | 1.48 | 17800 | 1465 | 12.1502 | 14500 | 1696 | 8.5495 | 10.24 | Split_Wall_Mounted Ugine 1.48TR SEER 10.24 | Split_Wall_Mounted Ugine 1.48TR SEER 10.23
96 | Split_Wall_Mounted | Zamil | MAZ18CCXAD1 | Non-Inverter | 1.5 | 1.49 | 17998.294 | 1440 | 12.4988 | 15899.9147 | 1849 | 8.5992 | 10.53 | Split_Wall_Mounted Zamil 1.49TR SEER 10.53 | Split_Wall_Mounted Zamil 1.49TR SEER 10.52
97 | Split_Wall_Mounted | Zamil | ADO18CHX0D | Non-Inverter | 1.5 | 1.49 | 17998.294 | 1379 | 13.0517 | 15295.9909 | 1700 | 8.9976 | 10.97 | Split_Wall_Mounted Zamil 1.49TR SEER 10.97 | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
98 | Split_Wall_Mounted | LG | NF182H2 | Inverter | 1.5 | 1.5 | 18000 | 1452 | 12.3967 | 15300 | 1759 | 8.6981 | 10.47 | Split_Wall_Mounted LG 1.5TR SEER 10.47 | Inverter unit "No replacement"
99 | Split_Wall_Mounted | General | GC-18KFC | Non-Inverter | 1.5 | 1.5 | 18000 | 1500 | 12 | 15500 | 1824 | 8.4978 | 10.17 | Split_Wall_Mounted General 1.5TR SEER 10.17 | Split_Wall_Mounted General 1.5TR SEER 10.16
100 | Split_Wall_Mounted | Mando | MP-SER-18C | Non-Inverter | 1.5 | 1.5 | 18000 | 1469 | 12.2532 | 15500 | 1802 | 8.6016 | 10.36 | Split_Wall_Mounted Mando 1.5TR SEER 10.36 | Split_Wall_Mounted Mando 1.5TR SEER 10.35
101 | Split_Wall_Mounted | Unix | Omr/split 18H | Non-Inverter | 1.5 | 1.5 | 18000 | 1500 | 12 | 15500 | 1824 | 8.4978 | 10.17 | Split_Wall_Mounted Unix 1.5TR SEER 10.17 | Split_Wall_Mounted General 1.5TR SEER 10.16
102 | Split_Wall_Mounted | Royal_Temp | MIS-180-HP | Non-Inverter | 1.5 | 1.5 | 18000 | 2045 | 8.802 | 15732 | 2280 | 6.9 | 7.67 | Split_Wall_Mounted Royal_Temp 1.5TR SEER 7.67 | Split_Wall_Mounted Royal Temp 1.5TR SEER 7.67
103 | Split_Wall_Mounted | Carrier | 42SXC180 | Non-Inverter | 1.5 | 1.5 | 18000 | 1379 | 13.0529 | 15000 | 1667 | 8.9982 | 10.95 | Split_Wall_Mounted Carrier 1.5TR SEER 10.95 | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
104 | Split_Wall_Mounted | Gree | GWC18MC | Non-Inverter | 1.5 | 1.5 | 18083 | 2250 | 8.0369 | 16200 | 2550 | 6.3529 | 7.04 | Split_Wall_Mounted Gree 1.5TR SEER 7.04 | Split_Wall_Mounted Gree 1.5TR SEER 7.03
105 | Split_Wall_Mounted | Zamil | TAL18CHXED | Non-Inverter | 1.5 | 1.5 | 18100 | 1496 | 12.0989 | 15470 | 1800 | 8.5944 | 10.26 | Split_Wall_Mounted Zamil 1.5TR SEER 10.26 | Split_Wall_Mounted Cooline 1.5TR SEER 10.25
106 | Split_Wall_Mounted | LG | Y182SH / GS-H1825SA4 | Non-Inverter | 1.5 | 1.52 | 18254.1939 | 1900 | 9.6075 | 15183.3949 | 2200 | 6.9015 | 8.15 | Split_Wall_Mounted LG 1.52TR SEER 8.15 | Split_Wall_Mounted LG 1.52TR SEER 8.15
107 | Split_Wall_Mounted | LG | Y182NH / GS-H1825SA4 | Non-Inverter | 1.5 | 1.52 | 18254.1939 | 1900 | 9.6075 | 15183.3949 | 2200 | 6.9015 | 8.15 | Split_Wall_Mounted LG 1.52TR SEER 8.15 | Split_Wall_Mounted LG 1.52TR SEER 8.15
108 | Split_Wall_Mounted | LG | S18TQC / HSNC186C4B0 | Non-Inverter | 1.5 | 1.53 | 18400 | 1919 | 9.5883 | 16200 | 2218 | 7.3039 | 8.3 | Split_Wall_Mounted LG 1.53TR SEER 8.3 | Split_Wall_Mounted LG 1.53TR SEER 8.30
109 | Split_Wall_Mounted | Okia | OKA-18CJ | Non-Inverter | 1.5 | 1.53 | 18400 | 1510 | 12.1854 | 15800 | 1800 | 8.7778 | 10.37 | Split_Wall_Mounted Okia 1.53TR SEER 10.37 | Split_Wall_Mounted Okia 1.53TR SEER 10.37
110 | Split_Wall_Mounted | LG | Y182SC / GS-C1825SA4 | Non-Inverter | 1.5 | 1.54 | 18561 | 1950 | 9.5185 | 16036 | 2300 | 6.9722 | 8.14 | Split_Wall_Mounted LG 1.54TR SEER 8.14 | Split_Wall_Mounted LG 1.54TR SEER 8.14
111 | Split_Wall_Mounted | Daikin | RY18HEVLK / FTY18HEVLK | Non-Inverter | 1.5 | 1.55 | 18650 | 2260 | 8.2522 | 16100 | 2630 | 6.1217 | 7.08 | Split_Wall_Mounted Daikin 1.55TR SEER 7.08 | Split_Wall_Mounted Daikin 1.55TR SEER 7.08
112 | Split_Wall_Mounted | LG | Y242NH / GS-H2425SA4 | Non-Inverter | 2 | 1.74 | 20949.673 | 2200 | 9.5226 | 18254.1939 | 2550 | 7.1585 | 8.21 | Split_Wall_Mounted LG 1.74TR SEER 8.21 | Split_Wall_Mounted LG 1.74TR SEER 8.20
113 | Split_Wall_Mounted | LG | B2427H / DSNH24257B1 | Non-Inverter | 2 | 1.74 | 20949.673 | 1820 | 11.5108 | 18936.5937 | 2280 | 8.3055 | 9.84 | Split_Wall_Mounted LG 1.74TR SEER 9.84 | Split_Wall_Mounted LG 1.74TR SEER 9.84
114 | Split_Wall_Mounted | LG | Y242SH N54 | Non-Inverter | 2 | 1.74 | 20949.673 | 2200 | 9.5226 | 18254.1939 | 2550 | 7.1585 | 8.21 | Split_Wall_Mounted LG 1.74TR SEER 8.21 | Split_Wall_Mounted LG 1.74TR SEER 8.20
115 | Split_Wall_Mounted | ARROW | RO-24CBA22-H | Non-Inverter | 2 | 1.75 | 21000 | 1710 | 12.2807 | 17900 | 2060 | 8.6893 | 10.4 | Split_Wall_Mounted ARROW 1.75TR SEER 10.4 | Split_Wall_Mounted Arrow 1.75TR SEER 10.39
116 | Split_Wall_Mounted | Giant | GIANT-24C | Non-Inverter | 2 | 1.75 | 21000 | 1750 | 12 | 18900 | 2100 | 9 | 10.36 | Split_Wall_Mounted Giant 1.75TR SEER 10.36 | Split_Wall_Mounted Giant 1.75TR SEER 10.36
117 | Split_Wall_Mounted | Carrier | 38HQR24US30-04 | Non-Inverter | 2 | 1.75 | 21000 | 2400 | 8.75 | 18500 | 2700 | 6.8519 | 7.63 | Split_Wall_Mounted Carrier 1.75TR SEER 7.63 | Split_Wall_Mounted Carrier 1.75TR SEER 7.63
118 | Split_Wall_Mounted | LG | S242DC N51 | Non-Inverter | 2 | 1.79 | 21495.5928 | 2500 | 8.5982 | 18765.9937 | 3000 | 6.2553 | 7.35 | Split_Wall_Mounted LG 1.79TR SEER 7.35 | Split_Wall_Mounted Carrier 1.79TR SEER 8.31
119 | Split_Wall_Mounted | Crown | CROWN 24C | Non-Inverter | 2 | 1.79 | 21500 | 1770 | 12.1469 | 18600 | 2130 | 8.7324 | 10.34 | Split_Wall_Mounted Crown 1.79TR SEER 10.34 | Split_Wall_Mounted Crown 1.79TR SEER 10.33
120 | Split_Wall_Mounted | Carrier | 38MQR18US33-04 | Non-Inverter | 2 | 1.79 | 21500 | 2240 | 9.5982 | 19000 | 2600 | 7.3077 | 8.31 | Split_Wall_Mounted Carrier 1.79TR SEER 8.31 | Split_Wall_Mounted Carrier 1.79TR SEER 8.31
121 | Split_Wall_Mounted | Carrier | 38HKR24US30-04 | Non-Inverter | 2 | 1.81 | 21750 | 2400 | 9.0625 | 19500 | 2750 | 7.0909 | 7.91 | Split_Wall_Mounted Carrier 1.81TR SEER 7.91 | Split_Wall_Mounted Carrier 1.81TR SEER 7.91
122 | Split_Wall_Mounted | LG | B242PC | Non-Inverter | 2 | 1.82 | 21870.9127 | 1900 | 11.511 | 18970.7137 | 2290 | 8.2842 | 9.8 | Split_Wall_Mounted LG 1.82TR SEER 9.8 | Split_Wall_Mounted LG 1.99TR SEER 9.80
123 | Split_Wall_Mounted | Zamil | MLZ24CHIXFTR | Non-Inverter | 2 | 1.83 | 21997.1567 | 2558 | 8.5994 | 19499.5735 | 2868 | 6.799 | 7.52 | Split_Wall_Mounted Zamil 1.83TR SEER 7.52 | Split_Wall_Mounted Zamil 1.83TR SEER 7.51
124 | Split_Wall_Mounted | LG | NS242H2 | Non-Inverter | 2 | 1.83 | 22000 | 1818 | 12.1012 | 18500 | 2127 | 8.6977 | 10.28 | Split_Wall_Mounted LG 1.83TR SEER 10.28 | Split_Wall_Mounted LG 1.83TR SEER 10.27
125 | Split_Wall_Mounted | Gree | GWC24AGE-D3NTA1A/O | Non-Inverter | 2 | 1.83 | 22000 | 1818 | 12.1012 | 18300 | 2178 | 8.4022 | 10.17 | Split_Wall_Mounted Gree 1.83TR SEER 10.17 | Split_Wall_Mounted Gree 1.83TR SEER 10.17
126 | Split_Wall_Mounted | Super_General | KSGS245GER | Non-Inverter | 2 | 1.83 | 22000 | 1781 | 12.3526 | 18400 | 2114 | 8.7039 | 10.43 | Split_Wall_Mounted Super_General 1.83TR SEER 10.43 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
127 | Split_Wall_Mounted | Carrier | 42SKC243-2S | Non-Inverter | 2 | 1.83 | 22000 | 1833 | 12.0022 | 18500 | 2229 | 8.2997 | 10.09 | Split_Wall_Mounted Carrier 1.83TR SEER 10.09 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
128 | Split_Wall_Mounted | Mando | MP-NF23-24C/H | Non-Inverter | 2 | 1.84 | 22100 | 1804 | 12.2506 | 18500 | 2189 | 8.4513 | 10.29 | Split_Wall_Mounted Mando 1.84TR SEER 10.29 | Split_Wall_Mounted Mando 1.84TR SEER 10.28
129 | Split_Wall_Mounted | Midea | MSTEP24CRNAG2 | Non-Inverter | 2 | 1.84 | 22100 | 1804 | 12.2506 | 18500 | 2189 | 8.4513 | 10.29 | Split_Wall_Mounted Midea 1.84TR SEER 10.29 | Split_Wall_Mounted Mando 1.84TR SEER 10.28
130 | Split_Wall_Mounted | Carrier | 38HVBS024-3032B | Non-Inverter | 2 | 1.84 | 22100 | 1830 | 12.0765 | 19300 | 2320 | 8.319 | 10.17 | Split_Wall_Mounted Carrier 1.84TR SEER 10.17 | Split_Wall_Mounted Carrier 1.84TR SEER 10.16
131 | Split_Wall_Mounted | Fisher | FSAC-FT24CERAN | Non-Inverter | 2 | 1.91 | 23000 | 1917 | 11.9979 | 19800 | 2329 | 8.5015 | 10.17 | Split_Wall_Mounted Fisher 1.91TR SEER 10.17 | Split_Wall_Mounted Carrier 1.84TR SEER 10.16
132 | Split_Wall_Mounted | Carrier | 38PQR24US33-08 | Non-Inverter | 2 | 1.91 | 23000 | 1991 | 11.552 | 20000 | 2410 | 8.2988 | 9.84 | Split_Wall_Mounted Carrier 1.91TR SEER 9.84 | Split_Wall_Mounted Carrier 1.92TR SEER 9.83
133 | Split_Wall_Mounted | Carrier | 38PQS24US33-01 | Non-Inverter | 2 | 1.91 | 23000 | 1990 | 11.5578 | 20000 | 2410 | 8.2988 | 9.84 | Split_Wall_Mounted Carrier 1.91TR SEER 9.84 | Split_Wall_Mounted Carrier 1.92TR SEER 9.83
134 | Split_Wall_Mounted | Carrier | 42QHMT24N-308J | Non-Inverter | 2 | 1.91 | 23000 | 1991 | 11.552 | 20000 | 2410 | 8.2988 | 9.84 | Split_Wall_Mounted Carrier 1.91TR SEER 9.84 | Split_Wall_Mounted Carrier 1.92TR SEER 9.83
135 | Split_Wall_Mounted | Zamil | ADX24EHAXFQ | Non-Inverter | 2 | 1.95 | 23491 | 2975 | 7.8961 | 18994 | 3325 | 5.7125 | 6.7 | Split_Wall_Mounted Zamil 1.95TR SEER 6.7 | Split_Wall_Mounted Zamil 2TR SEER 6.69
136 | Split_Wall_Mounted | Zamil | ADU24CHAXFV | Non-Inverter | 2 | 1.95 | 23498.4362 | 2460 | 9.5522 | 20100.0853 | 2935 | 6.8484 | 8.12 | Split_Wall_Mounted Zamil 1.95TR SEER 8.12 | Split_Wall_Mounted Zamil 1.95TR SEER 8.11
137 | Split_Wall_Mounted | LG | A3024HNV0 | Non-Inverter | 2 | 1.99 | 23986.352 | 2080 | 11.5319 | 20779.0731 | 2510 | 8.2785 | 9.81 | Split_Wall_Mounted LG 1.99TR SEER 9.81 | Split_Wall_Mounted LG 1.99TR SEER 9.80
138 | Split_Wall_Mounted | Zamil | ADO24CHXOW | Non-Inverter | 2 | 1.99 | 23996.588 | 2078 | 11.5479 | 19299.0752 | 2325 | 8.3007 | 9.77 | Split_Wall_Mounted Zamil 1.99TR SEER 9.77 | Split_Wall_Mounted Zamil 1.99TR SEER9.77
139 | Split_Wall_Mounted | Zamil | KRC24CDMHJOW | Non-Inverter | 2 | 1.99 | 23996.588 | 2078 | 11.5479 | 19298.2656 | 2325 | 8.3003 | 9.77 | Split_Wall_Mounted Zamil 1.99TR SEER 9.77 | Split_Wall_Mounted Zamil 1.99TR SEER9.77
140 | Split_Wall_Mounted | LG | S242WQ / LSUH2425WM1 | Non-Inverter | 2 | 2 | 24000 | 2600 | 9.2308 | 19653 | 2840 | 6.9201 | 7.91 | Split_Wall_Mounted LG 2TR SEER 7.91 | Split_Wall_Mounted Carrier 1.81TR SEER 7.91
141 | Split_Wall_Mounted | Daewoo | DSA-240LH-R | Non-Inverter | 2 | 2 | 24000 | 2500 | 9.6 | 17496.7302 | 2800 | 6.2488 | 7.86 | Split_Wall_Mounted Daewoo 2TR SEER 7.86 | Split_Wall_Mounted DAEWOO 2TR SEER 7.86
142 | Split_Wall_Mounted | Royal_Temp | MIS-240-HP | Non-Inverter | 2 | 2 | 24000 | 2727 | 8.8009 | 20064 | 2907 | 6.902 | 7.64 | Split_Wall_Mounted Royal_Temp 2TR SEER 7.64 | Split_Wall_Mounted Gree 1.83TR SEER 10.17
143 | Split_Wall_Mounted | Carrier | 42QCF02433 | Non-Inverter | 2 | 2 | 24000 | 2450 | 9.7959 | 21000 | 2650 | 7.9245 | 8.61 | Split_Wall_Mounted Carrier 2TR SEER 8.61 | Split_Wall_Mounted Carrier 2TR SEER 8.60
144 | Split_Wall_Mounted | Zamil | KRZ26CDACIED | Non-Inverter | 2 | 2 | 24055 | 1935 | 12.4315 | 19960 | 2353 | 8.4828 | 10.4 | Split_Wall_Mounted Zamil 2TR SEER 10.4 | Split_Wall_Mounted Zamil 2TR SEER 10.39
145 | Split_Wall_Mounted | Mitsubishi | PK-2.5FLD | Non-Inverter | 2 | 2.03 | 24400 | 3010 | 8.1063 | 22700 | 3540 | 6.4124 | 7.12 | Split_Wall_Mounted Mitsubishi 2.03TR SEER 7.12 | Split_Wall_Mounted Zamil 1.95TR SEER 8.11
146 | Split_Wall_Mounted | Zamil | MWZ30CHIXFTQ/KZC30CSIHAMCQ | Non-Inverter | 2 | 2.11 | 25398.9195 | 3050 | 8.3275 | 21997.1567 | 3375 | 6.5177 | 7.25 | Split_Wall_Mounted Zamil 2.11TR SEER 7.25 | Split_Wall_Mounted LG 2.21TR SEER 8.14
147 | Split_Wall_Mounted | Zamil | HWU30EHAYFV | Non-Inverter | 2 | 2.12 | 25497.8675 | 2670 | 9.5498 | 21099.801 | 3080 | 6.8506 | 8.1 | Split_Wall_Mounted Zamil 2.12TR SEER 8.1 | Split_Wall_Mounted Zamil 1.99TR SEER9.77
148 | Split_Wall_Mounted | Gree | GWC30QE-D3NTN4A/I | Non-Inverter | 2 | 2.19 | 26300 | 2230 | 11.7937 | 22800 | 2680 | 8.5075 | 10.05 | Split_Wall_Mounted Gree 2.19TR SEER 10.05 | Split_Wall_Mounted Gree 2.25TR SEER 11.11
149 | Split_Wall_Mounted | LG | S3228Q / LS-H322V8C2 | Non-Inverter | 2 | 2.21 | 26613.5911 | 2790 | 9.5389 | 23713.3921 | 3450 | 6.8734 | 8.14 | Split_Wall_Mounted LG 2.21TR SEER 8.14 | Split_Wall_Mounted LG 2.21TR SEER 8.14
150 | Split_Wall_Mounted | LG | S3224H NV2 | Non-Inverter | 2 | 2.21 | 26613.5911 | 2790 | 9.5389 | 23713.3921 | 3450 | 6.8734 | 8.14 | Split_Wall_Mounted LG 2.21TR SEER 8.14 | Split_Wall_Mounted Gree 2.25TR SEER 11.11
151 | Split_Wall_Mounted | Zamil | ADO30CHXCD | Non-Inverter | 2 | 2.24 | 26954.791 | 2195 | 12.2801 | 23798.6921 | 2800 | 8.4995 | 10.36 | Split_Wall_Mounted Zamil 2.24TR SEER 10.36 | Split_Wall_Mounted Gree 2.25TR SEER 11.11
152 | Split_Wall_Mounted | LG | S322GC SD3 | Non-Inverter | 2 | 2.24 | 26988.911 | 3210 | 8.4078 | 23747.5121 | 3690 | 6.4356 | 7.29 | Split_Wall_Mounted LG 2.24TR SEER 7.29 | Split_Wall_Mounted LG 2.25TR SEER 7.28
153 | Split_Wall_Mounted | Gree | GWC30QF-S3DTB2A/O | Non-Inverter | 2 | 2.25 | 27000 | 2080 | 12.9808 | 23200 | 2430 | 9.5473 | 11.11 | Split_Wall_Mounted Gree 2.25TR SEER 11.11 | Split_Wall_Mounted Gree 2.25TR SEER 11.11
154 | Split_Wall_Mounted | Okia | OKA-30CH | Non-Inverter | 2 | 2.25 | 27000 | 2160 | 12.5 | 23200 | 2620 | 8.855 | 10.59 | Split_Wall_Mounted Okia 2.25TR SEER 10.59 | Split_Wall_Mounted Okia 2.25TR SEER 10.59
155 | Split_Wall_Mounted | LG | ATNQ30GPLT4 | Inverter | 2 | 2.25 | 27000 | 2180 | 12.3853 | 24000 | 2760 | 8.6957 | 10.5 | Split_Wall_Mounted LG 2.25TR SEER 10.5 | Inverter unit "No replacement"
156 | Split_Wall_Mounted | Carrier | 42QTD024VS | Non-Inverter | 2 | 2.25 | 27000 | 2250 | 12 | 24000 | 2810 | 8.5409 | 10.21 | Split_Wall_Mounted Carrier 2.25TR SEER 10.21 | Split_Wall_Mounted Carrier 2.25TR SEER 10.20
157 | Split_Wall_Mounted | Fuji | RSA30FRTA-S | Non-Inverter | 2 | 2.29 | 27500 | 2700 | 10.1852 | 24000 | 3290 | 7.2948 | 8.67 | Split_Wall_Mounted Fuji 2.29TR SEER 8.67 | Split_Wall_Mounted Fuji 2.2TR SEER 8.66
158 | Split_Wall_Mounted | LG | T3224H / AS-W322V4B0 | Non-Inverter | 2.5 | 2.33 | 27978.3907 | 2320 | 12.0597 | 24600.5118 | 2650 | 9.2832 | 10.47 | Split_Wall_Mounted LG 2.33TR SEER 10.47 | Split_Wall_Mounted LG 2.33TR SEER 10.46
159 | Split_Wall_Mounted | LG | T3224C / AS-Q322V4B0 | Inverter | 2.5 | 2.33 | 27978.3907 | 2240 | 12.4904 | 22382.7125 | 2510 | 8.9174 | 10.55 | Split_Wall_Mounted LG 2.33TR SEER 10.55 | Inverter unit "No replacement"
160 | Split_Wall_Mounted | Samsung | AR30JVFUCWKX | Non-Inverter | 2.5 | 2.33 | 28000 | 2430 | 11.5226 | 25000 | 3010 | 8.3056 | 9.84 | Split_Wall_Mounted Samsung 2.33TR SEER 9.84 | Split_Wall_Mounted Samsung 2.33TR SEER 9.83
161 | Split_Wall_Mounted | Zamil | ADO30CHXCW | Non-Inverter | 2.5 | 2.35 | 28295.7066 | 2450 | 11.5493 | 25296.5596 | 3048 | 8.2994 | 9.86 | Split_Wall_Mounted Zamil 2.35TR SEER 9.86 | Split_Wall_Mounted Zamil 2.35TR SEER 9.85
162 | Split_Wall_Mounted | LG | NT382H / S4-W32R43FA | Non-Inverter | 2.5 | 2.5 | 30000 | 2440 | 12.2951 | 25400 | 2885 | 8.8042 | 10.44 | Split_Wall_Mounted LG 2.5TR SEER 10.44 | Split_Wall_Mounted LG 2.5TR SEER 10.43
163 | Split_Wall_Mounted | Royal_Temp | MIS-300-HP | Non-Inverter | 2.5 | 2.5 | 30000 | 3448 | 8.7007 | 24396 | 3587 | 6.8012 | 7.53 | Split_Wall_Mounted Royal_Temp 2.5TR SEER 7.53 | Split_Wall_Mounted Royal Temp 2.5TR SEER 7.53
164 | Split_Wall_Mounted | Carrier | 42QHB030HS | Non-Inverter | 2.5 | 2.58 | 31000 | 2520 | 12.3016 | 26500 | 3050 | 8.6885 | 10.41 | Split_Wall_Mounted Carrier 2.58TR SEER 10.41 | Split_Wall_Mounted Carrier 2.58TR SEER 10.41
165 | Split_Wall_Mounted | LG | T3624C / AS-Q362V4V0 | Non-Inverter | 2.5 | 2.58 | 31015.0697 | 2710 | 11.4447 | 24805.2317 | 2960 | 8.3801 | 9.73 | Split_Wall_Mounted LG 2.58TR SEER 9.73 | Split_Wall_Mounted LG 2.58TR SEER 9.72
166 | Split_Wall_Mounted | LG | T3624H / AS-W362V4V0 | Non-Inverter | 2.5 | 2.58 | 31015.0697 | 2720 | 11.4026 | 24771.1117 | 2920 | 8.4833 | 9.73 | Split_Wall_Mounted LG 2.58TR SEER 9.73 | Split_Wall_Mounted LG 2.58TR SEER 9.73
167 | Split_Wall_Mounted | LG | S382GH / LS-H382DSB0 | Non-Inverter | 2.5 | 2.6 | 31219.7896 | 3800 | 8.2157 | 27466.5908 | 4220 | 6.5087 | 7.19 | Split_Wall_Mounted LG 2.6TR SEER 7.19 | Split_Wall_Mounted LG 2.6TR SEER 7.18
168 | Split_Wall_Mounted | LG | S3624H NV2 | Non-Inverter | 2.5 | 2.61 | 31390.3895 | 3300 | 9.5122 | 28319.5906 | 4130 | 6.857 | 8.13 | Split_Wall_Mounted LG 2.61TR SEER 8.13 | Split_Wall_Mounted LG 2.62TR SEER 8.13
169 | Split_Wall_Mounted | Royal_Temp | MIS-320-HP | Non-Inverter | 2.5 | 2.66 | 32000 | 3720 | 8.6022 | 26380 | 3937 | 6.7005 | 7.45 | Split_Wall_Mounted Royal_Temp 2.66TR SEER 7.45 | Split_Wall_Mounted Royal Temp 2.67TR SEER 7.44
170 | Split_Wall_Mounted | Carrier | 38XP100H3PE/ 42XP100H3PE | Non-Inverter | 3 | 2.75 | 33000 | 3309.9298 | 9.97 | 29500 | 4057.7717 | 7.27 | 8.54 | Split_Wall_Mounted Carrier 2.75TR SEER 8.54 | Split_Wall_Mounted Carrier 2.75TR SEER 8.54
171 | Split_Wall_Mounted | Carrier | 38XP100H3-E | Non-Inverter | 3 | 2.75 | 33000 | 3200 | 10.3125 | 29500 | 3950 | 7.4684 | 8.82 | Split_Wall_Mounted Carrier 2.75TR SEER 8.82 | Split_Wall_Mounted Carrier 2.75TR SEER 8.81
172 | Split_Wall_Mounted | Daikin | FTY24HEVLK | Non-Inverter | 2 | 1.77 | 21350 | 2470 | 8.6437 | 18330 | 2770 | 6.6173 | 7.48 | Split_Wall_Mounted Daikin 1.77TR SEER 7.48 | Split_Wall_Mounted Daikin 1.78TR SEER 7.47
173 | Split_Wall_Mounted | Daikin | R30KEVLK / FT30KEVLK | Non-Inverter | 2 | 2.27 | 27300 | 2750 | 9.9273 | 24000 | 3200 | 7.5 | 8.57 | Split_Wall_Mounted Daikin 2.27TR SEER 8.57 | Split_Wall_Mounted Daikin 2.28TR SEER 8.57
174 | Split_Wall_Mounted | Carrier | 42XP100HP3P | Non-Inverter | 3 | 2.78 | 33438 | 3920.0469 | 8.53 | 29500 | 4097.2222 | 7.2 | 7.58 | Split_Wall_Mounted Carrier 2.78TR SEER 7.58 | Split_Wall_Mounted Carrier 2.75TR SEER 8.54
175 | Split_Wall_Mounted | Samsung | AS18FCN | Non-Inverter | 1.5 | 1.5 | 18000 | 1900 | 9.4737 | 15300 | 2250 | 6.8 | 8.05 | Split_Wall_Mounted Samsung 1.5TR SEER 8.05 | Split_Wall_Mounted LG 1.54TR SEER 8.14
176 | Split_Wall_Mounted | LG | S182NH | Non-Inverter | 1.5 | 1.5 | 18000 | 1900 | 9.4737 | 15593 | 2040 | 7.6436 | 8.31 | Split_Wall_Mounted LG 1.5TR SEER 8.31 | Split_Wall_Mounted LG 1.53TR SEER 8.30
177 | Split_Wall_Mounted | Mando | S-036H/S | Non-Inverter | 2 | 2.3 | 27600 | 2400 | 11.5 | 23900 | 2880 | 8.2986 | 9.8 | Split_Wall_Mounted Mando 2.3TR SEER 9.8 | Split_Wall_Mounted Samsung 2.33TR SEER 9.83
178 | Split_Wall_Mounted | Sky star | SKYSTARL-18C | Non-Inverter | 1.5 | 1.49 | 17913 | 1480 | 12.1034 | 15354 | 1760 | 8.7239 | 10.3 | Split_Wall_Mounted Sky star 1.49TR SEER 10.3 | Split_Wall_Mounted Mando 1.5TR SEER 10.35
179 | Split_Wall_Mounted | Champion | CHSSI-24C | Non-Inverter | 2 | 1.84 | 22178 | 2266.8919 | 9.7834 | 19637.6068 | 2733.2485 | 7.1847 | 8.39 | Split_Wall_Mounted Champion 1.84TR SEER 8.39 | Split_Wall_Mounted Carrier 1.79TR SEER 8.31
180 | Split_Wall_Mounted | Mando | S-030H/S | Non-Inverter | 2 | 2 | 24000 | 2080 | 11.5385 | 20500 | 2380 | 8.6134 | 9.91 | Split_Wall_Mounted Mando 2TR SEER 9.91 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
181 | Split_Wall_Mounted | Mando | KT3F-61GW/S | Non-Inverter | 2 | 1.73 | 20800 | 1800 | 11.5556 | 16700 | 2000 | 8.35 | 9.79 | Split_Wall_Mounted Mando 1.73TR SEER 9.79 | Split_Wall_Mounted LG 1.82TR SEER 9.79
182 | Split_Wall_Mounted | Mando | S030-HS | Non-Inverter | 2 | 2 | 24000 | 2080 | 11.5385 | 20500 | 2380 | 8.6134 | 9.91 | Split_Wall_Mounted Mando 2TR SEER 9.91 | Split_Wall_Mounted Carrier 1.92TR SEER 9.83
183 | Split_Wall_Mounted | Haam | HM24CSM23GO | Non-Inverter | 2 | 1.83 | 22000 | 1818 | 12.1012 | 19400 | 2230 | 8.6996 | 10.32 | Split_Wall_Mounted Haam 1.83TR SEER 10.32 | Split_Wall_Mounted Crown 1.79TR SEER 10.33
184 | Split_Wall_Mounted | TIT | TIS18CG | Non-Inverter | 1.5 | 1.5 | 18053 | 1529 | 11.8071 | 15630 | 1801 | 8.6785 | 10.11 | Split_Wall_Mounted TIT 1.5TR SEER 10.11 | Split_Wall_Mounted LG 1.47TR SEER 10.15
185 | Split_Wall_Mounted | Master_Cool | CSA-18CH | Non-Inverter | 1.5 | 1.44 | 17388 | 1950 | 8.9169 | 15384.6154 | 2250 | 6.8376 | 7.74 | Split_Wall_Mounted Master_Cool 1.44TR SEER 7.74 | Split_Wall_Mounted Royal Temp 1.5TR SEER 7.67
186 | Split_Wall_Mounted | LG | S242DC | Non-Inverter | 2 | 1.79 | 21496 | 2500 | 8.5984 | 18766 | 3000 | 6.2553 | 7.35 | Split_Wall_Mounted LG 1.79TR SEER 7.35 | Split_Wall_Mounted LG 1.79TR SEER 7.34
187 | Split_Wall_Mounted | Haam | KFR-51GW/a | Non-Inverter | 1.5 | 1.45 | 17400 | 1950 | 8.9231 | 15300 | 2250 | 6.8 | 7.73 | Split_Wall_Mounted Haam 1.45TR SEER 7.73 | Split_Wall_Mounted Royal Temp 1.5TR SEER 7.67
188 | Split_Wall_Mounted | Haas | HSA25CE6HM7 | Non-Inverter | 2 | 1.79 | 21500 | 1820 | 11.8132 | 18300 | 2180 | 8.3945 | 10.01 | Split_Wall_Mounted Haas 1.79TR SEER 10.01 | Split_Wall_Mounted Carrier 1.83TR SEER 10.08
189 | Split_Wall_Mounted | Samsung | AQ24UUPN | Non-Inverter | 2 | 2 | 24000 | 2600 | 9.2308 | 19841 | 2900 | 6.8417 | 7.89 | Split_Wall_Mounted Samsung 2TR SEER 7.89 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
190 | Split_Wall_Mounted | ARROW | RO-18JC | Non-Inverter | 1.5 | 1.53 | 18400 | 1510 | 12.1854 | 15800 | 1800 | 8.7778 | 10.37 | Split_Wall_Mounted ARROW 1.53TR SEER 10.37 | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
191 | Split_Wall_Mounted | Mando | MP920-24C | Non-Inverter | 2 | 1.83 | 22000 | 1781 | 12.3526 | 18200 | 2128 | 8.5526 | 10.37 | Split_Wall_Mounted Mando 1.83TR SEER 10.37 | Split_Wall_Mounted Giant 1.75TR SEER 10.36
192 | Split_Wall_Mounted | Haam | HM18CSM20 | Non-Inverter | 1.5 | 1.5 | 18000 | 1469 | 12.2532 | 15200 | 1747 | 8.7006 | 10.38 | Split_Wall_Mounted Haam 1.5TR SEER 10.38 | Split_Wall_Mounted Okia 1.53TR SEER 10.37
193 | Split_Wall_Mounted | Kelvinator | KMS18H9 | Non-Inverter | 1.5 | 1.5 | 18100 | 1484 | 12.1968 | 15900 | 1797 | 8.8481 | 10.42 | Split_Wall_Mounted Kelvinator 1.5TR SEER 10.42 | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
194 | Split_Wall_Mounted | York | Y4HFXH018BBA--FX | Non-Inverter | 1.5 | 1.45 | 17500 | 1800 | 9.7222 | 15500 | 2115 | 7.3286 | 8.4 | Split_Wall_Mounted York 1.45TR SEER 8.4 | Split_Wall_Mounted LG 1.5TR SEER 8.40
195 | Split_Wall_Mounted | LG | S242MHT0 | Non-Inverter | 2 | 2 | 24000 | 2500 | 9.6 | 20063 | 3035 | 6.6105 | 8.06 | Split_Wall_Mounted LG 2TR SEER 8.06 | Split_Wall_Mounted Zamil 1.99TR SEER9.77
196 | Split_Wall_Mounted | Gree | STW24KHR | Non-Inverter | 2 | 1.93 | 23202 | 2000 | 11.601 | 19899 | 2390 | 8.3259 | 9.86 | Split_Wall_Mounted Gree 1.93TR SEER 9.86 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
197 | Split_Wall_Mounted | Midea | MSTF24HR5F3 | Non-Inverter | 2 | 1.72 | 20642 | 2130 | 9.6911 | 19414.3 | 2450 | 7.9242 | 8.6 | Split_Wall_Mounted Midea 1.72TR SEER 8.6 | Split_Wall_Mounted Carrier 1.79TR SEER 8.31
198 | Split_Wall_Mounted | LG | S242SSHN52 | Non-Inverter | 2 | 1.79 | 21496 | 2700 | 7.9615 | 18425 | 3250 | 5.6692 | 6.76 | Split_Wall_Mounted LG 1.79TR SEER 6.76 | Split_Wall_Mounted Zamil 2TR SEER 6.69
199 | Split_Wall_Mounted | Icone | ico-18k/FC | Non-Inverter | 1.5 | 1.42 | 17060 | 1420 | 12.0141 | 14671 | 1700 | 8.63 | 10.22 | Split_Wall_Mounted Icone 1.42TR SEER 10.22 | Split_Wall_Mounted Ugine 1.48TR SEER 10.23
200 | Split_Wall_Mounted | Gree | GWH18MC-D1NTA8G/I | Non-Inverter | 1.5 | 1.46 | 17600 | 1796 | 9.7996 | 15200 | 2024 | 7.5099 | 8.48 | Split_Wall_Mounted Gree 1.46TR SEER 8.48 | Split_Wall_Mounted LG 1.5TR SEER 8.40
201 | Split_Wall_Mounted | Gree | GWC24ACE-D3NTA1C/I | Non-Inverter | 2 | 1.83 | 22000 | 1865 | 11.7962 | 18300 | 2200 | 8.3182 | 9.96 | Split_Wall_Mounted Gree 1.83TR SEER 9.96 | Split_Wall_Mounted LG 1.74TR SEER 9.84
202 | Split_Wall_Mounted | LG | S242KHST2 | Non-Inverter | 2 | 2 | 24000 | 2450 | 9.7959 | 19312 | 2850 | 6.7761 | 8.21 | Split_Wall_Mounted LG 2TR SEER 8.21 | Split_Wall_Mounted Zamil 1.95TR SEER 8.11
203 | Split_Wall_Mounted | Fuji | RSA24UMTA-S | Non-Inverter | 2 | 1.88 | 22600 | 1960 | 11.5306 | 19500 | 2350 | 8.2979 | 9.82 | Split_Wall_Mounted Fuji 1.88TR SEER 9.82 | Split_Wall_Mounted LG 1.99TR SEER 9.80
204 | Split_Wall_Mounted | LG | S182SCN51 | Non-Inverter | 1.5 | 1.45 | 17488 | 2050 | 8.5307 | 15184 | 2450 | 6.1976 | 7.29 | Split_Wall_Mounted LG 1.45TR SEER 7.29 | Split_Wall_Mounted LG 1.46TR SEER 7.28
205 | Split_Wall_Mounted | Speed_Cool | SCSGI180C | Non-Inverter | 1.5 | 1.5 | 18000 | 1525 | 11.8033 | 14900 | 1773 | 8.4038 | 9.99 | Split_Wall_Mounted Speed_Cool 1.5TR SEER 9.99 | Split_Wall_Mounted GREE 1.5TR SEER 9.98
206 | Split_Wall_Mounted | Gree | GWH24QE-D3NTB4D/I | Non-Inverter | 2 | 1.87 | 22500 | 1838 | 12.2416 | 18900 | 2228 | 8.4829 | 10.29 | Split_Wall_Mounted Gree 1.87TR SEER 10.29 | Split_Wall_Mounted Mando 1.84TR SEER 10.28
207 | Split_Wall_Mounted | Gree | GWH36QF-D3NTB4G/I | Non-Inverter | 2.5 | 2.65 | 31800 | 2650 | 12 | 27000 | 3173 | 8.5093 | 10.16 | Split_Wall_Mounted Gree 2.65TR SEER 10.16 | Split_Wall_Mounted Zamil 2.62TR SEER 10.00
208 | Split_Wall_Mounted | LG | A182WPNS2 | Non-Inverter | 1.5 | 1.5 | 18000 | 1950 | 9.2308 | 16787 | 2080 | 8.0707 | 8.32 | Split_Wall_Mounted LG 1.5TR SEER 8.32 | Split_Wall_Mounted LG 1.53TR SEER 8.30
209 | Split_Wall_Mounted | LG | S182SCN52 | Non-Inverter | 1.5 | 1.45 | 17489 | 2000 | 8.7445 | 15354 | 2300 | 6.6757 | 7.57 | Split_Wall_Mounted LG 1.45TR SEER 7.57 | Split_Wall_Mounted LG 1.46TR SEER 7.57
210 | Split_Wall_Mounted | TACHIAIR | TC18C/7S16 | Non-Inverter | 1.5 | 1.45 | 17400 | 1510 | 11.5232 | 14900 | 1730 | 8.6127 | 9.9 | Split_Wall_Mounted TACHIAIR 1.45TR SEER 9.9 | Split_Wall_Mounted Chigo 1.38TR SEER 9.88
211 | Split_Wall_Mounted | LG | B2424HN50 | Non-Inverter | 2 | 1.76 | 21196.5812 | 1830 | 11.5828 | 18903 | 2280 | 8.2908 | 9.87 | Split_Wall_Mounted LG 1.76TR SEER 9.87 | Split_Wall_Mounted LG 1.74TR SEER 9.84
212 | Split_Wall_Mounted | Midea | MSTM12CRN | Non-Inverter | 1 | 1.01 | 12171 | 1005 | 12.1104 | 10161 | 1187 | 8.5602 | 10.23 | Split_Wall_Mounted Midea 1.01TR SEER 10.23 | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
213 | Split_Wall_Mounted | Icone | ico-24k/fc | Non-Inverter | 2 | 1.79 | 21495 | 1800 | 11.9417 | 18425 | 2150 | 8.5698 | 10.15 | Split_Wall_Mounted Icone 1.79TR SEER 10.15 | Split_Wall_Mounted Carrier 1.84TR SEER 10.16
214 | Split_Wall_Mounted | LG | S242NHST0 | Non-Inverter | 2 | 1.91 | 22997 | 2630 | 8.7441 | 20063 | 3035 | 6.6105 | 7.55 | Split_Wall_Mounted LG 1.91TR SEER 7.55 | Split_Wall_Mounted LG 1.91TR SEER 7.54
215 | Split_Wall_Mounted | LG | S242DHN51 | Non-Inverter | 2 | 1.79 | 21496 | 2700 | 7.9615 | 18425 | 3250 | 5.6692 | 6.76 | Split_Wall_Mounted LG 1.79TR SEER 6.76 | Split_Wall_Mounted Zamil 2TR SEER 6.69
216 | Split_Wall_Mounted | Mando | KT3F-51G/S | Non-Inverter | 1.5 | 1.45 | 17400 | 1510 | 11.5232 | 14900 | 1730 | 8.6127 | 9.9 | Split_Wall_Mounted Mando 1.45TR SEER 9.9 | Split_Wall_Mounted Chigo 1.38TR SEER 9.88
217 | Split_Wall_Mounted | Gree | GWC24QE-D3NTBF/I | Non-Inverter | 2 | 1.83 | 22000 | 1880 | 11.7021 | 18700 | 2255 | 8.2927 | 9.91 | Split_Wall_Mounted Gree 1.83TR SEER 9.91 | Split_Wall_Mounted LG 1.74TR SEER 9.84
218 | Split_Wall_Mounted | Frego | FW18Y-2N7 | Non-Inverter | 1.5 | 1.49 | 17913 | 1480 | 12.1034 | 15354 | 1760 | 8.7239 | 10.3 | Split_Wall_Mounted Frego 1.49TR SEER 10.3 | Split_Wall_Mounted Mando 1.5TR SEER 10.35
219 | Split_Wall_Mounted | Haam | HM24CWM7S17 | Non-Inverter | 2 | 1.9 | 22800 | 1880 | 12.1277 | 19220 | 2210 | 8.6968 | 10.3 | Split_Wall_Mounted Haam 1.9TR SEER 10.3 | Split_Wall_Mounted Mando 1.84TR SEER 10.28
220 | Split_Wall_Mounted | Haam | HM24CSM22GO | Non-Inverter | 2 | 1.83 | 22000 | 1781 | 12.3526 | 18200 | 2128 | 8.5526 | 10.37 | Split_Wall_Mounted Haam 1.83TR SEER 10.37 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
221 | Split_Wall_Mounted | Haier | HSU-30LEG13(T3) | Non-Inverter | 2.5 | 2.5 | 30000 | 3500 | 8.5714 | 24500 | 3900 | 6.2821 | 7.3 | Split_Wall_Mounted Haier 2.5TR SEER 7.3 | Split_Wall_Mounted Royal Temp 2.5TR SEER 7.53
222 | Split_Wall_Mounted | Fuji | ROW-24RSD | Non-Inverter | 2 | 1.9 | 22800 | 2520 | 9.0476 | 19500 | 2900 | 6.7241 | 7.76 | Split_Wall_Mounted Fuji 1.9TR SEER 7.76 | Split_Wall_Mounted DAEWOO 2TR SEER 7.86
223 | Split_Wall_Mounted | Haam | HM24H/7S15 | Non-Inverter | 2 | 1.68 | 20200 | 1750 | 11.5429 | 17700 | 2120 | 8.3491 | 9.85 | Split_Wall_Mounted Haam 1.68TR SEER 9.85 | Split_Wall_Mounted LG 1.74TR SEER 9.84
224 | Split_Wall_Mounted | TIT | TIS-1820 C | Non-Inverter | 1.5 | 1.5 | 18000 | 1450 | 12.4138 | 15300 | 1760 | 8.6932 | 10.48 | Split_Wall_Mounted TIT 1.5TR SEER 10.48 | Split_Wall_Mounted LG 1.5TR SEER 10.46
225 | Split_Wall_Mounted | LG | S242SH | Non-Inverter | 2 | 1.78 | 21478 | 2700 | 7.9548 | 18425 | 3250 | 5.6692 | 6.75 | Split_Wall_Mounted LG 1.78TR SEER 6.75 | Split_Wall_Mounted Zamil 2TR SEER 6.69
226 | Split_Wall_Mounted | LG | S182KH | Non-Inverter | 1.5 | 1.5 | 18000 | 1900 | 9.4737 | 15593 | 2040 | 7.6436 | 8.31 | Split_Wall_Mounted LG 1.5TR SEER 8.31 | Split_Wall_Mounted LG 1.53TR SEER 8.30
227 | Split_Wall_Mounted | LG | S242NH | Non-Inverter | 2 | 1.91 | 22997 | 2630 | 8.7441 | 20063 | 3035 | 6.6105 | 7.55 | Split_Wall_Mounted LG 1.91TR SEER 7.55 | Split_Wall_Mounted LG 1.91TR SEER 7.54
228 | Split_Wall_Mounted | Haam | HM18C/7810 | Non-Inverter | 1.5 | 1.45 | 17400 | 1510 | 11.5232 | 14000 | 1730 | 8.0925 | 9.69 | Split_Wall_Mounted Haam 1.45TR SEER 9.69 | Split_Wall_Mounted LG 1.46TR SEER 9.8
229 | Split_Wall_Mounted | Union | UI24CV60LOFR | Non-Inverter | 2 | 1.79 | 21500 | 1870 | 11.4973 | 18000 | 2169 | 8.2988 | 9.77 | Split_Wall_Mounted Union 1.79TR SEER 9.77 | Split_Wall_Mounted LG 1.82TR SEER 9.79
230 | Split_Wall_Mounted | LG | Y242SHN54 | Non-Inverter | 2 | 1.74 | 20950 | 2200 | 9.5227 | 18254 | 2550 | 7.1584 | 8.21 | Split_Wall_Mounted LG 1.74TR SEER 8.21 | Split_Wall_Mounted LG 1.74TR SEER 8.20
231 | Split_Wall_Mounted | RANTIC | OMS24H | Non-Inverter | 2 | 1.83 | 22000 | 1850 | 11.8919 | 19600 | 2250 | 8.7111 | 10.2 | Split_Wall_Mounted RANTIC 1.83TR SEER 10.2 | Split_Wall_Mounted Gree 1.83TR SEER 10.17
232 | Split_Wall_Mounted | Haas | HSA25FE7HH7X | Non-Inverter | 2 | 1.91 | 23000 | 1925 | 11.9481 | 19800 | 2290 | 8.6463 | 10.18 | Split_Wall_Mounted Haas 1.91TR SEER 10.18 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
233 | Split_Wall_Mounted | Haas | HSA20FE7HH7X | Non-Inverter | 1.5 | 1.5 | 18000 | 1485 | 12.1212 | 15600 | 1785 | 8.7395 | 10.33 | Split_Wall_Mounted Haas 1.5TR SEER 10.33 | Split_Wall_Mounted Mando 1.5TR SEER 10.35
234 | Split_Wall_Mounted | Unix | GSDAD24HN | Non-Inverter | 2 | 1.71 | 20545 | 1739 | 11.8143 | 17577 | 1827 | 9.6207 | 10.38 | Split_Wall_Mounted Unix 1.71TR SEER 10.38 | Split_Wall_Mounted Giant 1.75TR SEER 10.36
235 | Split_Wall_Mounted | BASIC | BSACL-F24C7 | Non-Inverter | 2 | 1.84 | 22178 | 1820 | 12.1857 | 19107 | 2200 | 8.685 | 10.34 | Split_Wall_Mounted BASIC 1.84TR SEER 10.34 | Split_Wall_Mounted Crown 1.79TR SEER 10.33
236 | Split_Wall_Mounted | Gree | GWH12AGC-D3NTAIA/I | Non-Inverter | 1 | 0.96 | 11600 | 970 | 11.9588 | 10000 | 1170 | 8.547 | 10.16 | Split_Wall_Mounted Gree 0.96TR SEER 10.16 | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
237 | Split_Wall_Mounted | LG | NS182H2NK0 | Inverter | 1.5 | 1.5 | 18000 | 1452 | 12.3967 | 15300 | 1759 | 8.6981 | 10.47 | Split_Wall_Mounted LG 1.5TR SEER 10.47 | Inverter unit "No replacement"
238 | Split_Wall_Mounted | Samsung | AR24HPFNBWKN | Non-Inverter | 2 | 1.93 | 23200 | 2340 | 9.9145 | 20230 | 2700 | 7.4926 | 8.56 | Split_Wall_Mounted Samsung 1.93TR SEER 8.56 | Split_Wall_Mounted LG 1.74TR SEER 9.84
239 | Split_Wall_Mounted | Mando | KT3F-61G/S | Non-Inverter | 2 | 1.73 | 20800 | 1800 | 11.5556 | 16700 | 2000 | 8.35 | 9.79 | Split_Wall_Mounted Mando 1.73TR SEER 9.79 | Split_Wall_Mounted LG 1.82TR SEER 9.79
240 | Split_Wall_Mounted | Haam | HM18C/7815 | Non-Inverter | 1.5 | 1.45 | 17400 | 1510 | 11.5232 | 14900 | 1730 | 8.6127 | 9.9 | Split_Wall_Mounted Haam 1.45TR SEER 9.9 | Split_Wall_Mounted Chigo 1.38TR SEER 9.88
241 | Split_Wall_Mounted | Zamil | MA224CHXAD1 | Non-Inverter | 2 | 1.83 | 22000 | 1781 | 12.3526 | 18434.188 | 2114 | 8.7201 | 10.44 | Split_Wall_Mounted Zamil 1.83TR SEER 10.44 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
242 | Split_Wall_Mounted | LG | S242 NH STO | Non-Inverter | 2 | 1.91 | 22997 | 2630 | 8.7441 | 20063 | 3035 | 6.6105 | 7.55 | Split_Wall_Mounted LG 1.91TR SEER 7.55 | Split_Wall_Mounted LG 1.91TR SEER 7.54
243 | Split_Wall_Mounted | LG | S242SH N52 | Non-Inverter | 2 | 1.79 | 21496 | 2700 | 7.9615 | 18425 | 3250 | 5.6692 | 6.76 | Split_Wall_Mounted LG 1.79TR SEER 6.76 | Split_Wall_Mounted Zamil 2TR SEER 6.69
244 | Split_Wall_Mounted | Fuji | RSA24RAT | Non-Inverter | 2 | 1.88 | 22600 | 2520 | 8.9683 | 19500 | 2900 | 6.7241 | 7.72 | Split_Wall_Mounted Fuji 1.88TR SEER 7.72 | Split_Wall_Mounted Royal Temp 2TR SEER 7.64
245 | Split_Wall_Mounted | Dansat | DSA18WC | Non-Inverter | 1.5 | 1.44 | 17300 | 1400 | 12.3571 | 14700 | 1680 | 8.75 | 10.46 | Split_Wall_Mounted Dansat 1.44TR SEER 10.46 | Split_Wall_Mounted LG 1.5TR SEER 10.46
246 | Split_Wall_Mounted | LG | S242DH N51 | Non-Inverter | 2 | 1.79 | 21496 | 2700 | 7.9615 | 18425 | 3250 | 5.6692 | 6.76 | Split_Wall_Mounted LG 1.79TR SEER 6.76 | Split_Wall_Mounted Zamil 2TR SEER 6.69
247 | Split_Wall_Mounted | Dansat | DS1850C | Non-Inverter | 1.5 | 1.45 | 17400 | 1470 | 11.8367 | 14800 | 1780 | 8.3146 | 10 | Split_Wall_Mounted Dansat 1.45TR SEER 10 | Split_Wall_Mounted GREE 1.5TR SEER 9.98
248 | Split_Wall_Mounted | NIKAI | NSAC12136C22 | Non-Inverter | 1 | 1.02 | 12300 | 1030 | 11.9417 | 10800 | 1250 | 8.64 | 10.19 | Split_Wall_Mounted NIKAI 1.02TR SEER 10.19 | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
249 | Split_Wall_Mounted | Carrier | 42XP090H3P | Non-Inverter | 2.5 | 2.37 | 28551 | 3160 | 9.0351 | 24500 | 3398 | 7.2101 | 7.9 | Split_Wall_Mounted Carrier 2.37TR SEER 7.9 | Split_Wall_Mounted Zamil 2.35TR SEER 9.85
250 | Split_Wall_Mounted | Mando | MP920-36C | Non-Inverter | 2.5 | 2.61 | 31400 | 2614 | 12.0122 | 26800 | 3135 | 8.5486 | 10.19 | Split_Wall_Mounted Mando 2.61TR SEER 10.19 | Split_Wall_Mounted Zamil 2.62TR SEER 10.00
251 | Split_Wall_Mounted | LG | Y242SH | Non-Inverter | 2 | 1.74 | 20950 | 2200 | 9.5227 | 18084 | 2550 | 7.0918 | 8.18 | Split_Wall_Mounted LG 1.74TR SEER 8.18 | Split_Wall_Mounted LG 1.74TR SEER 8.17
252 | Split_Wall_Mounted | LG | LS-H242TKA2 | Non-Inverter | 2 | 2 | 24000 | 2450 | 9.7959 | 19278 | 2850 | 6.7642 | 8.2 | Split_Wall_Mounted LG 2TR SEER 8.2 | Split_Wall_Mounted Zamil 1.95TR SEER 8.11
253 | Split_Wall_Mounted | Gree | GWH24ACE-D3NTA1B/I | Non-Inverter | 2 | 1.84 | 22100 | 1840 | 12.0109 | 19100 | 2213 | 8.6308 | 10.22 | Split_Wall_Mounted Gree 1.84TR SEER 10.22 | Split_Wall_Mounted LG 1.83TR SEER 10.27
254 | Split_Wall_Mounted | Gree | GWH30ACE-D3NTA1D/I | Non-Inverter | 2 | 2.27 | 27300 | 2310 | 11.8182 | 23000 | 2705 | 8.5028 | 10.04 | Split_Wall_Mounted Gree 2.27TR SEER 10.04 | Split_Wall_Mounted GREE 2.19TR SEER 10.05
255 | Split_Wall_Mounted | Carrier | 42QHC018-3P | Non-Inverter | 1.5 | 1.5 | 18000 | 1895 | 9.4987 | 16500 | 2260 | 7.3009 | 8.27 | Split_Wall_Mounted Carrier 1.5TR SEER 8.27 | Split_Wall_Mounted LG 1.53TR SEER 8.30
256 | Split_Wall_Mounted | York | YORX-18CC | Non-Inverter | 1.5 | 1.49 | 17913 | 1480 | 12.1034 | 15354 | 1760 | 8.7239 | 10.3 | Split_Wall_Mounted York 1.49TR SEER 10.3 | Split_Wall_Mounted Mando 1.5TR SEER 10.35
257 | Split_Wall_Mounted | LG | S242LC | Non-Inverter | 2 | 2 | 24000 | 2350 | 10.2128 | 19722 | 2700 | 7.3044 | 8.65 | Split_Wall_Mounted LG 2TR SEER 8.65 | Split_Wall_Mounted Carrier 2TR SEER 8.60
258 | Split_Wall_Mounted | Starway | FOSW18CSP | Non-Inverter | 1.5 | 1.43 | 17200 | 1470 | 11.7007 | 14500 | 1690 | 8.5799 | 9.99 | Split_Wall_Mounted Starway 1.43TR SEER 9.99 | Split_Wall_Mounted GREE 1.5TR SEER 9.98
259 | Split_Wall_Mounted | Speed_Cool | SCSG180C | Non-Inverter | 1.5 | 1.5 | 18000 | 1525 | 11.8033 | 14900 | 1773 | 8.4038 | 9.99 | Split_Wall_Mounted Speed_Cool 1.5TR SEER 9.99 | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
260 | Split_Wall_Mounted | Haam | HM18CSM23GO | Non-Inverter | 1.5 | 1.52 | 18300 | 1476 | 12.3984 | 15900 | 1807 | 8.7991 | 10.52 | Split_Wall_Mounted Haam 1.52TR SEER 10.52 | Split_Wall_Mounted Zamil 1.49TR SEER 10.52
261 | Split_Wall_Mounted | STARWAY | ACSW24KC | Non-Inverter | 2 | 1.91 | 23000 | 1855 | 12.3989 | 19800 | 2275 | 8.7033 | 10.48 | Split_Wall_Mounted STARWAY 1.91TR SEER 10.48 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
262 | Split_Wall_Mounted | Fuji | FOJ30SCO | Non-Inverter | 2 | 2 | 24000 | 2080 | 11.5385 | 20500 | 2380 | 8.6134 | 9.91 | Split_Wall_Mounted Fuji 2TR SEER 9.91 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
263 | Split_Wall_Mounted | Haam | HM18CWM7S17 | Non-Inverter | 1.5 | 1.53 | 18400 | 1560 | 11.7949 | 16600 | 1860 | 8.9247 | 10.21 | Split_Wall_Mounted Haam 1.53TR SEER 10.21 | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
264 | Split_Wall_Mounted | Haam | HM30C/7S15 | Non-Inverter | 2 | 2 | 24000 | 2080 | 11.5385 | 20500 | 2380 | 8.6134 | 9.91 | Split_Wall_Mounted Haam 2TR SEER 9.91 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
265 | Split_Wall_Mounted | TACHIAIR | TC12C/7S16 | Non-Inverter | 1 | 1.01 | 12225 | 1060 | 11.533 | 10416 | 1240 | 8.4 | 9.84 | Split_Wall_Mounted TACHIAIR 1.01TR SEER 9.84 | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
266 | Split_Wall_Mounted | LG | NF122C0 | Inverter | 1 | 1 | 12000 | 968 | 12.3967 | 10000 | 1150 | 8.6957 | 10.45 | Split_Wall_Mounted LG 1TR SEER 10.45 | Inverter unit "No replacement"
267 | Split_Wall_Mounted | LG | NS242C3NK1 | Inverter | 2 | 1.79 | 21500 | 1734 | 12.3991 | 18500 | 2127 | 8.6977 | 10.48 | Split_Wall_Mounted LG 1.79TR SEER 10.48 | Inverter unit "No replacement"
268 | Split_Wall_Mounted | Mando | KT3FR-61G/S | Non-Inverter | 2 | 1.68 | 20200 | 1750 | 11.5429 | 17700 | 2130 | 8.3099 | 9.84 | Split_Wall_Mounted Mando 1.68TR SEER 9.84 | Split_Wall_Mounted LG 1.74TR SEER 9.84
269 | Split_Wall_Mounted | Haam | HM18C/7S16 | Non-Inverter | 1.5 | 1.45 | 17400 | 1510 | 11.5232 | 14900 | 1730 | 8.6127 | 9.9 | Split_Wall_Mounted Haam 1.45TR SEER 9.9 | Split_Wall_Mounted Chigo 1.38TR SEER 9.88
270 | Split_Wall_Mounted | LG | NV242H1NK0 | Inverter | 1.5 | 1.66 | 20000 | 1613 | 12.3993 | 17000 | 1954 | 8.7001 | 10.47 | Split_Wall_Mounted LG 1.66TR SEER 10.47 | Inverter unit "No replacement"
271 | Split_Wall_Mounted | AUX | AUX24H | Non-Inverter | 2 | 1.84 | 22178 | 1820 | 12.1857 | 19107 | 2200 | 8.685 | 10.34 | Split_Wall_Mounted AUX 1.84TR SEER 10.34 | Split_Wall_Mounted Crown 1.79TR SEER 10.33
272 | Split_Wall_Mounted | Zamil | MAZ24CCXAD1 | Non-Inverter | 2 | 1.83 | 22000 | 1781 | 12.3526 | 18434.188 | 2114 | 8.7201 | 10.44 | Split_Wall_Mounted Zamil 1.83TR SEER 10.44 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
273 | Split_Wall_Mounted | Mando | KT3FR-36GW/S | Non-Inverter | 1 | 1.01 | 12225 | 1050 | 11.6429 | 10416 | 1240 | 8.4 | 9.91 | Split_Wall_Mounted Mando 1.01TR SEER 9.91 | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
274 | Split_Wall_Mounted | Union | UI18CV60L0FR | Non-Inverter | 1.5 | 1.45 | 17500 | 1522 | 11.498 | 15000 | 1796 | 8.3519 | 9.81 | Split_Wall_Mounted Union 1.45TR SEER 9.81 | Split_Wall_Mounted LG 1.46TR SEER 9.8
275 | Split_Wall_Mounted | LG | LS-H242TLB2 | Non-Inverter | 2 | 2 | 24000 | 2450 | 9.7959 | 19278 | 2850 | 6.7642 | 8.2 | Split_Wall_Mounted LG 2TR SEER 8.2 | Split_Wall_Mounted Zamil 1.95TR SEER 8.11
276 | Split_Wall_Mounted | LG | Y242NH N04 | Non-Inverter | 2 | 1.74 | 20950 | 2200 | 9.5227 | 18254 | 2550 | 7.1584 | 8.21 | Split_Wall_Mounted LG 1.74TR SEER 8.21 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
277 | Split_Wall_Mounted | AMAX | SAC12AX | Non-Inverter | 1 | 1.02 | 12300 | 1010 | 12.1782 | 10600 | 1260 | 8.4127 | 10.25 | Split_Wall_Mounted AMAX 1.02TR SEER 10.25 | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
278 | Split_Wall_Mounted | Craft | DS18FE7HY7WM | Non-Inverter | 1.5 | 1.47 | 17650 | 1525 | 11.5738 | 14750 | 1760 | 8.3807 | 9.84 | Split_Wall_Mounted Craft 1.47TR SEER 9.84 | Split_Wall_Mounted LG 1.45TR SEER 9.84
279 | Split_Wall_Mounted | Craft | DS24FE7HY7WM | Non-Inverter | 2 | 1.9 | 22800 | 1950 | 11.6923 | 19300 | 2320 | 8.319 | 9.91 | Split_Wall_Mounted Craft 1.9TR SEER 9.91 | Split_Wall_Mounted LG 1.74TR SEER 9.84
280 | Split_Wall_Mounted | Haam | HM18CSM19N | Non-Inverter | 1.5 | 1.5 | 18000 | 1488 | 12.0968 | 15900 | 1843 | 8.6272 | 10.29 | Split_Wall_Mounted Haam 1.5TR SEER 10.29 | Split_Wall_Mounted Cooline 1.5TR SEER 10.25
281 | Split_Wall_Mounted | Zamil | MRZ24CDGCIAD1 | Non-Inverter | 2 | 1.83 | 22000 | 1781 | 12.3526 | 18434.188 | 2114 | 8.7201 | 10.44 | Split_Wall_Mounted Zamil 1.83TR SEER 10.44 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
282 | Split_Wall_Mounted | Mando | KT3F-51GW/S | Non-Inverter | 1.5 | 1.45 | 17400 | 1810 | 9.6133 | 14300 | 1960 | 7.2959 | 8.27 | Split_Wall_Mounted Mando 1.45TR SEER 8.27 | Split_Wall_Mounted LG 1.53TR SEER 8.30
283 | Split_Wall_Mounted | Starway | SW18KCN | Non-Inverter | 1.5 | 1.43 | 17244 | 1437 | 12 | 15012 | 1691 | 8.8776 | 10.3 | Split_Wall_Mounted Starway 1.43TR SEER 10.3 | Split_Wall_Mounted Cooline 1.5TR SEER 10.25
284 | Split_Wall_Mounted | Telezone | TZ18C1 | Non-Inverter | 1.5 | 1.44 | 17300 | 1430 | 12.0979 | 14000 | 1710 | 8.1871 | 10.08 | Split_Wall_Mounted Telezone 1.44TR SEER 10.08 | Split_Wall_Mounted LG 1.47TR SEER 10.15
285 | Split_Wall_Mounted | Zamil | MAZ24GCXAD1. | Non-Inverter | 2 | 1.83 | 22008.3159 | 1781 | 12.3573 | 18220.8383 | 2128 | 8.5624 | 10.38 | Split_Wall_Mounted Zamil 1.83TR SEER 10.38 | Split_Wall_Mounted Giant 1.75TR SEER 10.36
286 | Split_Wall_Mounted | Ugine | UGNPSM18C-A | Non-Inverter | 1.5 | 1.52 | 18353 | 1526 | 12.0269 | 16516 | 1827 | 9.04 | 10.39 | Split_Wall_Mounted Ugine 1.52TR SEER 10.39 | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
287 | Split_Wall_Mounted | Zamil | MAZ23CHXAD1 | Non-Inverter | 2 | 1.83 | 22000 | 1781 | 12.3526 | 18400 | 2114 | 8.7039 | 10.43 | Split_Wall_Mounted Zamil 1.83TR SEER 10.43 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
288 | Split_Wall_Mounted | Gree | GWC12ACC-D3NTA1E/I | Non-Inverter | 1 | 1 | 12000 | 1005 | 11.9403 | 10200 | 1172 | 8.7031 | 10.19 | Split_Wall_Mounted Gree 1TR SEER 10.19 | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
289 | Split_Wall_Mounted | Frego | FW18Y2H22 | Non-Inverter | 1.5 | 1.44 | 17300 | 1430 | 12.0979 | 14900 | 1710 | 8.7135 | 10.3 | Split_Wall_Mounted Frego 1.44TR SEER 10.3 | Split_Wall_Mounted Cooline 1.5TR SEER 10.25
290 | Split_Wall_Mounted | LG | Y242SC | Non-Inverter | 2 | 1.74 | 20984 | 2200 | 9.5382 | 18254 | 2600 | 7.0208 | 8.18 | Split_Wall_Mounted LG 1.74TR SEER 8.18 | Split_Wall_Mounted LG 1.74TR SEER 8.17
291 | Split_Wall_Mounted | TCL | TAC-30CHS/JC6 | Non-Inverter | 2 | 2.04 | 24500 | 2110 | 11.6114 | 19790 | 2385 | 8.2977 | 9.82 | Split_Wall_Mounted TCL 2.04TR SEER 9.82 | Split_Wall_Mounted LG 1.99TR SEER 9.80
292 | Split_Wall_Mounted | BeSat | BSSF18CHD | Non-Inverter | 1.5 | 1.42 | 17100 | 1390 | 12.3022 | 14500 | 1665 | 8.7087 | 10.41 | Split_Wall_Mounted BeSat 1.42TR SEER 10.41 | Split_Wall_Mounted Mando 1.53TR SEER 10.38
293 | Split_Wall_Mounted | TACHIAIR | TC18C/7316 | Non-Inverter | 1.5 | 1.45 | 17400 | 1510 | 11.5232 | 14900 | 1730 | 8.6127 | 9.9 | Split_Wall_Mounted TACHIAIR 1.45TR SEER 9.9 | Split_Wall_Mounted Chigo 1.38TR SEER 9.88
294 | Split_Wall_Mounted | Mando | KT3F-51W/S | Non-Inverter | 1.5 | 1.45 | 17400 | 1510 | 11.5232 | 14900 | 1730 | 8.6127 | 9.9 | Split_Wall_Mounted Mando 1.45TR SEER 9.9 | Split_Wall_Mounted Chigo 1.38TR SEER 9.88
295 | Split_Wall_Mounted | Craft | DSN24FE7YTAI | Non-Inverter | 2 | 2 | 24000 | 1832 | 13.1004 | 23000 | 2754 | 8.3515 | 10.85 | Split_Wall_Mounted Craft 2TR SEER 10.85 | Split_Wall_Mounted Zamil 2TR SEER 10.39
296 | Split_Wall_Mounted | Haas | HSA25FE7HH7 | Non-Inverter | 2 | 1.91 | 23000 | 1925 | 11.9481 | 19800 | 2290 | 8.6463 | 10.18 | Split_Wall_Mounted Haas 1.91TR SEER 10.18 | Split_Wall_Mounted Gree 1.83TR SEER 10.17
297 | Split_Wall_Mounted | LG | S242LH | Non-Inverter | 2 | 2 | 24000 | 2450 | 9.7959 | 19278 | 2850 | 6.7642 | 8.2 | Split_Wall_Mounted LG 2TR SEER 8.2 | Split_Wall_Mounted Zamil 1.95TR SEER 8.11
298 | Split_Wall_Mounted | Falcon | FQS36C8 | Non-Inverter | 2.5 | 2.5 | 30000 | 2440 | 12.2951 | 25600 | 2940 | 8.7075 | 10.41 | Split_Wall_Mounted Falcon 2.5TR SEER 10.41 | Split_Wall_Mounted Carrier 2.58TR SEER 10.41
299 | Split_Wall_Mounted | Lakes | LSAC-12H/A | Non-Inverter | 1 | 0.9 | 10918 | 1200 | 9.0983 | 9553 | 1400 | 6.8236 | 7.84 | Split_Wall_Mounted Lakes 0.9TR SEER 7.84 | Split_Wall_Mounted LG 0.95TR SEER 7.9
300 | Split_Wall_Mounted | LG | LS-C242TLB2 | Non-Inverter | 2 | 2 | 24000 | 2350 | 10.2128 | 19722.1808 | 2700 | 7.3045 | 8.65 | Split_Wall_Mounted LG 2TR SEER 8.65 | Split_Wall_Mounted Carrier 2TR SEER 8.60
301 | Split_Wall_Mounted | LG | S182KC ST2 | Non-Inverter | 1.5 | 1.5 | 18000 | 1900 | 9.4737 | 16002.946 | 2080 | 7.6937 | 8.34 | Split_Wall_Mounted LG 1.5TR SEER 8.34 | Split_Wall_Mounted LG 1.46TR SEER 9.8
302 | Split_Wall_Mounted | Haas | HSA20FE6HH7N | Non-Inverter | 1.5 | 1.5 | 18000 | 1485 | 12.1212 | 15600 | 1785 | 8.7395 | 10.33 | Split_Wall_Mounted Haas 1.5TR SEER 10.33 | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
303 | Split_Wall_Mounted | Falcon | FQS12C8 | Non-Inverter | 1 | 0.99 | 11900 | 975 | 12.2051 | 10000 | 1150 | 8.6957 | 10.34 | Split_Wall_Mounted Falcon 0.99TR SEER 10.34 | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
304 | Split_Wall_Mounted | LG | Y182SC / X182EC | Non-Inverter | 1.5 | 1.54 | 18562 | 1950 | 9.519 | 16037 | 2300 | 6.9726 | 8.14 | Split_Wall_Mounted LG 1.54TR SEER 8.14 | Split_Wall_Mounted LG 1.46TR SEER 9.8
305 | Split_Wall_Mounted | Bancool | BC18CHL | Non-Inverter | 1.5 | 1.49 | 17913 | 1480 | 12.1034 | 15354 | 1760 | 8.7239 | 10.3 | Split_Wall_Mounted Bancool 1.49TR SEER 10.3 | Split_Wall_Mounted Mando 1.5TR SEER 10.35
306 | Split_Wall_Mounted | Ugine | UTS24LSRN-7 | Non-Inverter | 2 | 1.83 | 22000 | 1880 | 11.7021 | 18700 | 2255 | 8.2927 | 9.91 | Split_Wall_Mounted Ugine 1.83TR SEER 9.91 | Split_Wall_Mounted LG 1.74TR SEER 9.84
307 | Split_Wall_Mounted | Craft | DSA20FE7GR7 | Non-Inverter | 1.5 | 1.5 | 18000 | 1525 | 11.8033 | 14900 | 1773 | 8.4038 | 9.99 | Split_Wall_Mounted Craft 1.5TR SEER 9.99 | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
308 | Split_Wall_Mounted | LG | T242SH | Non-Inverter | 2 | 1.91 | 22929 | 2690 | 8.5238 | 20302 | 3010 | 6.7449 | 7.46 | Split_Wall_Mounted LG 1.91TR SEER 7.46 | Split_Wall_Mounted Daikin 1.78TR SEER 7.47
309 | Split_Wall_Mounted | LG | S3224H | Non-Inverter | 2 | 2.21 | 26614 | 2700 | 9.857 | 23714 | 3450 | 6.8736 | 8.34 | Split_Wall_Mounted LG 2.21TR SEER 8.34 | Split_Wall_Mounted Zamil 2.35TR SEER 9.85
310 | Split_Wall_Mounted | LG | S182 MH | Non-Inverter | 1.5 | 1.49 | 17981.9883 | 2060 | 8.7291 | 15491.1247 | 2870 | 5.3976 | 7.12 | Split_Wall_Mounted LG 1.49TR SEER 7.12 | Split_Wall_Mounted Daikin 1.55TR SEER 7.08
311 | Split_Wall_Mounted | Panasonic | CU-YW24WKS | Non-Inverter | 2 | 1.75 | 21000 | 1721 | 12.2022 | 19200 | 2207 | 8.6996 | 10.41 | Split_Wall_Mounted Panasonic 1.75TR SEER 10.41 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
312 | Split_Wall_Mounted | Gree | GWH24ACE-D3NTA1G/O | Non-Inverter | 2 | 1.83 | 22500 | 1838 | 12.2416 | 18900 | 2228 | 8.4829 | 10.29 | Split_Wall_Mounted Gree 1.83TR SEER 10.29 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
313 | Split_Wall_Mounted | LG | X242EH | Non-Inverter | 2 | 1.71 | 20539 | 2160 | 9.5088 | 17743 | 2530 | 7.013 | 8.15 | Split_Wall_Mounted LG 1.71TR SEER 8.15 | Split_Wall_Mounted LG 1.82TR SEER 9.79
314 | Split_Wall_Mounted | Gree | GWC24QE-D3NTB4F/O | Non-Inverter | 2 | 1.85 | 22250 | 1838 | 12.1055 | 18900 | 2228 | 8.4829 | 10.22 | Split_Wall_Mounted Gree 1.85TR SEER 10.22 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
315 | Split_Wall_Mounted | LG | S242SCN52 | Non-Inverter | 2 | 1.83 | 22015.32 | 2500 | 8.8061 | 17060.71 | 3000 | 5.6869 | 7.22 | Split_Wall_Mounted LG 1.83TR SEER 7.22 | Split_Wall_Mounted Carrier 2TR SEER 8.60
316 | Split_Wall_Mounted | York | YHFE24XT3CFE-R3 | Non-Inverter | 2 | 1.91 | 23000 | 1870 | 12.2995 | 19800 | 2275 | 8.7033 | 10.42 | Split_Wall_Mounted York 1.91TR SEER 10.42 | Split_Wall_Mounted Zamil 1.83TR SEER 10.42
317 | Split_Wall_Mounted | Mando | KT3FR-81GW/S | Non-Inverter | 2 | 1.68 | 20200 | 1750 | 11.5429 | 17700 | 2130 | 8.3099 | 9.84 | Split_Wall_Mounted Mando 1.68TR SEER 9.84 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
318 | Split_Wall_Mounted | MTC | MTC18C/7S-C17 | Non-Inverter | 1.5 | 1.45 | 17400 | 1510 | 11.5232 | 14900 | 1730 | 8.6127 | 9.9 | Split_Wall_Mounted MTC 1.45TR SEER 9.9 | Split_Wall_Mounted Chigo 1.38TR SEER 9.88
319 | Split_Wall_Mounted | Comfort | MSAC-18CS/GT7 | Non-Inverter | 1.5 | 1.46 | 17530 | 1510 | 11.6093 | 15695 | 1950 | 8.0487 | 9.81 | Split_Wall_Mounted Comfort 1.46TR SEER 9.81 | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
320 | Split_Wall_Mounted | New_house | YST3-30CR-D2 | Non-Inverter | 2 | 2.26 | 27200 | 2230 | 12.1973 | 22600 | 2613 | 8.6491 | 10.31 | Split_Wall_Mounted New_house 2.26TR SEER 10.31 | Split_Wall_Mounted Zamil 2.24TR SEER 10.35
321 | Split_Wall_Mounted | Haam | HN24H1ST16 | Non-Inverter | 2 | 1.68 | 20200 | 1750 | 11.5429 | 17700 | 2130 | 8.3099 | 9.84 | Split_Wall_Mounted Haam 1.68TR SEER 9.84 | Split_Wall_Mounted LG 1.74TR SEER 9.84
322 | Split_Wall_Mounted | Haam | HM24CSM19N | Non-Inverter | 2 | 1.84 | 22100 | 1811 | 12.2032 | 18400 | 2152 | 8.5502 | 10.28 | Split_Wall_Mounted Haam 1.84TR SEER 10.28 | Split_Wall_Mounted Mando 1.84TR SEER 10.28
323 | Split_Wall_Mounted | Mando | S-093H/S | Non-Inverter | 1.5 | 1.53 | 18400 | 1484 | 12.3989 | 16200 | 1800 | 9 | 10.6 | Split_Wall_Mounted Mando 1.53TR SEER 10.6 | Split_Wall_Mounted Zamil 1.49TR SEER 10.52
324 | Split_Wall_Mounted | Haam | HM24C/7S16 | Non-Inverter | 2 | 1.73 | 20800 | 1800 | 11.5556 | 16700 | 2000 | 8.35 | 9.79 | Split_Wall_Mounted Haam 1.73TR SEER 9.79 | Split_Wall_Mounted LG 1.82TR SEER 9.79
325 | Split_Wall_Mounted | LG | S242LH ST2 | Non-Inverter | 2 | 2 | 24000 | 2450 | 9.7959 | 19278.6023 | 2850 | 6.7644 | 8.2 | Split_Wall_Mounted LG 2TR SEER 8.2 | Split_Wall_Mounted Zamil 1.95TR SEER 8.11
326 | Split_Wall_Mounted | LG | FEZ24C | Non-Inverter | 2 | 1.91 | 22999 | 1991 | 11.5515 | 20010 | 2410 | 8.3029 | 9.84 | Split_Wall_Mounted LG 1.91TR SEER 9.84 | Split_Wall_Mounted Carrier 1.92TR SEER 9.83
327 | Split_Wall_Mounted | Champion | CHSSI-24H | Non-Inverter | 2 | 1.86 | 22349.5301 | 2560 | 8.7303 | 19610 | 3055 | 6.419 | 7.49 | Split_Wall_Mounted Champion 1.86TR SEER 7.49 | Split_Wall_Mounted Daikin 1.78TR SEER 7.47
328 | Split_Wall_Mounted | LG | LS-H182TKA2 | Non-Inverter | 1.5 | 1.5 | 18000 | 1900 | 9.4737 | 15609 | 2040 | 7.6515 | 8.31 | Split_Wall_Mounted LG 1.5TR SEER 8.31 | Split_Wall_Mounted LG 1.53TR SEER 8.30
329 | Split_Wall_Mounted | LG | B2424C | Non-Inverter | 2 | 1.82 | 21871.8302 | 1900 | 11.5115 | 18971.5095 | 2290 | 8.2845 | 9.8 | Split_Wall_Mounted LG 1.82TR SEER 9.8 | Split_Wall_Mounted LG 1.99TR SEER 9.80
330 | Split_Wall_Mounted | LG | X2A2EH | Non-Inverter | 2 | 1.88 | 22588.38 | 2160 | 10.4576 | 17743.1384 | 2530 | 7.0131 | 8.67 | Split_Wall_Mounted LG 1.88TR SEER 8.67 | Split_Wall_Mounted Carrier 2TR SEER 8.60
331 | Split_Wall_Mounted | Mando | AC-24H-MPZ | Non-Inverter | 2 | 2 | 24000 | 2000 | 12 | 20230.6601 | 2330 | 8.6827 | 10.21 | Split_Wall_Mounted Mando 2TR SEER 10.21 | Split_Wall_Mounted Gree 1.83TR SEER 10.17
332 | Split_Wall_Mounted | LG | S122SC | Non-Inverter | 1 | 0.91 | 10983 | 1290 | 8.514 | 9383.3905 | 1490 | 6.2976 | 7.3 | Split_Wall_Mounted LG 0.91TR SEER 7.3 | Split_Wall_Mounted LG 0.95TR SEER 7.9
333 | Split_Wall_Mounted | LG | S242NC | Non-Inverter | 2 | 1.95 | 23492 | 2750 | 8.5425 | 21496.4946 | 3270 | 6.5739 | 7.44 | Split_Wall_Mounted LG 1.95TR SEER 7.44 | Split_Wall_Mounted Daikin 1.78TR SEER 7.47
334 | Split_Wall_Mounted | LG | S242KC | Non-Inverter | 2 | 2 | 24000 | 2350 | 10.2128 | 19722.1808 | 2700 | 7.3045 | 8.65 | Split_Wall_Mounted LG 2TR SEER 8.65 | Split_Wall_Mounted Carrier 2TR SEER 8.60
335 | Split_Wall_Mounted | Midea | M3TEP18CRNMB2 | Non-Inverter | 1.5 | 1.54 | 18500 | 1590 | 11.6352 | 16500 | 1850 | 8.9189 | 10.1 | Split_Wall_Mounted Midea 1.54TR SEER 10.1 | Split_Wall_Mounted LG 1.47TR SEER 10.15
336 | Split_Wall_Mounted | LG | Y182NH | Non-Inverter | 1.5 | 1.52 | 18251 | 1900 | 9.6058 | 15187 | 2200 | 6.9032 | 8.15 | Split_Wall_Mounted LG 1.52TR SEER 8.15 | Split_Wall_Mounted LG 1.52TR SEER 8.15
337 | Split_Wall_Mounted | LG | B2424C | Non-Inverter | 2 | 1.82 | 21871.8302 | 1900 | 11.5115 | 18971.5095 | 2290 | 8.2845 | 9.8 | Split_Wall_Mounted LG 1.82TR SEER 9.8 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
338 | Split_Wall_Mounted | LG | T242SC | Non-Inverter | 2 | 1.91 | 22999 | 2550 | 9.0192 | 20641 | 3000 | 6.8803 | 7.82 | Split_Wall_Mounted LG 1.91TR SEER 7.82 | Split_Wall_Mounted DAEWOO 2TR SEER 7.86
339 | Split_Wall_Mounted | LG | Y242NC N54 | Non-Inverter | 2 | 1.74 | 20984.6733 | 2200 | 9.5385 | 18254.9597 | 2800 | 6.5196 | 8.01 | Split_Wall_Mounted LG 1.74TR SEER 8.01 | Split_Wall_Mounted Carrier 1.81TR SEER 7.91
340 | Split_Wall_Mounted | LG | S242SH N51 | Non-Inverter | 2 | 1.87 | 22520.1372 | 2640 | 8.5304 | 18947.5 | 3250 | 5.83 | 7.15 | Split_Wall_Mounted LG 1.87TR SEER 7.15 | Split_Wall_Mounted Carrier 2TR SEER 8.60
341 | Split_Wall_Mounted | LG | X242EC NC4 | Non-Inverter | 2 | 1.74 | 20984.6733 | 2200 | 9.5385 | 18254.9597 | 2600 | 7.0211 | 8.18 | Split_Wall_Mounted LG 1.74TR SEER 8.18 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
342 | Split_Wall_Mounted | LG | B2424C N51 | Non-Inverter | 2 | 1.82 | 21865 | 1900 | 11.5079 | 18965 | 2290 | 8.2817 | 9.8 | Split_Wall_Mounted LG 1.82TR SEER 9.8 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
343 | Split_Wall_Mounted | LG | X242SH NC3 | Non-Inverter | 2 | 1.71 | 20541.0948 | 2160 | 9.5098 | 17743.1384 | 2530 | 7.0131 | 8.15 | Split_Wall_Mounted LG 1.71TR SEER 8.15 | Split_Wall_Mounted LG 1.54TR SEER 8.14
344 | Split_Wall_Mounted | Carrier | 38QKB0303 | Non-Inverter | 2 | 2.25 | 27000 | 2213 | 12.2006 | 23000 | 2614 | 8.7988 | 10.38 | Split_Wall_Mounted Carrier 2.25TR SEER 10.38 | Split_Wall_Mounted Gree 2.25TR SEER 11.11
345 | Split_Wall_Mounted | LG | S242NH | Non-Inverter | 2 | 1.91 | 22997.8371 | 2630 | 8.7444 | 20063.395 | 3035 | 6.6107 | 7.55 | Split_Wall_Mounted LG 1.91TR SEER 7.55 | Split_Wall_Mounted Carrier 2TR SEER 8.60
346 | Split_Wall_Mounted | LG | S242DH | Non-Inverter | 2 | 1.79 | 21496.4946 | 2700 | 7.9617 | 18425.5668 | 3250 | 5.6694 | 6.76 | Split_Wall_Mounted LG 1.79TR SEER 6.76 | Split_Wall_Mounted Zamil 2TR SEER 6.69
347 | Split_Wall_Mounted | YONAN | KTF9R-24GWIi | Non-Inverter | 2 | 2 | 24000 | 2450 | 9.7959 | 22000 | 2900 | 7.5862 | 8.55 | Split_Wall_Mounted YONAN 2TR SEER 8.55 | Split_Wall_Mounted Carrier 2TR SEER 8.60
348 | Split_Wall_Mounted | LG | S242SC N51 | Non-Inverter | 2 | 1.87 | 22520.1372 | 2640 | 8.5304 | 18835.0238 | 3000 | 6.2783 | 7.29 | Split_Wall_Mounted LG 1.87TR SEER 7.29 | Split_Wall_Mounted LG 1.79TR SEER 7.34
349 | Split_Wall_Mounted | O2 | OSA-18KC7 | Non-Inverter | 1.5 | 1.53 | 18400 | 1510 | 12.1854 | 15800 | 1800 | 8.7778 | 10.37 | Split_Wall_Mounted O2 1.53TR SEER 10.37 | Split_Wall_Mounted Okia 1.53TR SEER 10.37
350 | Split_Wall_Mounted | Frego | FW12X2H9 | Non-Inverter | 1 | 1.02 | 12300 | 1010 | 12.1782 | 10600 | 1260 | 8.4127 | 10.25 | Split_Wall_Mounted Frego 1.02TR SEER 10.25 | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
351 | Split_Wall_Mounted | General | GC-18K/LK | Non-Inverter | 1.5 | 1.53 | 18400 | 1510 | 12.1854 | 15800 | 1800 | 8.7778 | 10.37 | Split_Wall_Mounted General 1.53TR SEER 10.37 | Split_Wall_Mounted Okia 1.53TR SEER 10.37
352 | Split_Wall_Mounted | Lakes | LSAC-12C/6S | Non-Inverter | 1 | 1.01 | 12225 | 1060 | 11.533 | 10416 | 1240 | 8.4 | 9.84 | Split_Wall_Mounted Lakes 1.01TR SEER 9.84 | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
353 | Split_Wall_Mounted | Midea | MSTO26HRNM10 | Non-Inverter | 2 | 2.04 | 24563 | 2092 | 11.7414 | 21396 | 2496 | 8.5721 | 10.04 | Split_Wall_Mounted Midea 2.04TR SEER 10.04 | Split_Wall_Mounted GREE 2.19TR SEER 10.05
354 | Split_Wall_Mounted | LG | A182SH NC0 | Non-Inverter | 1.5 | 1.42 | 17060.71 | 1480 | 11.5275 | 14740.4534 | 1780 | 8.2812 | 9.81 | Split_Wall_Mounted LG 1.42TR SEER 9.81 | Split_Wall_Mounted LG 1.46TR SEER 9.8
355 | Split_Wall_Mounted | Samsung | AQ24TULN | Non-Inverter | 2 | 2 | 24000 | 2600 | 9.2308 | 19841.6036 | 2900 | 6.8419 | 7.89 | Split_Wall_Mounted Samsung 2TR SEER 7.89 | Split_Wall_Mounted Carrier 1.81TR SEER 7.91
356 | Split_Wall_Mounted | Samsung | AQ18UUPN | Non-Inverter | 1.5 | 1.5 | 18000 | 1900 | 9.4737 | 15278.0348 | 2250 | 6.7902 | 8.05 | Split_Wall_Mounted Samsung 1.5TR SEER 8.05 | Split_Wall_Mounted LG 1.54TR SEER 8.14
357 | Split_Wall_Mounted | KELON | KHS24H | Non-Inverter | 2 | 1.91 | 23000 | 1925 | 11.9481 | 19800 | 2290 | 8.6463 | 10.18 | Split_Wall_Mounted KELON 1.91TR SEER 10.18 | Split_Wall_Mounted Gree 1.83TR SEER 10.17
358 | Split_Wall_Mounted | LG | Y24SH | Non-Inverter | 2 | 1.74 | 20950.5519 | 2200 | 9.523 | 18254.9597 | 2550 | 7.1588 | 8.21 | Split_Wall_Mounted LG 1.74TR SEER 8.21 | Split_Wall_Mounted LG 1.74TR SEER 8.20
359 | Split_Wall_Mounted | AUX | AUX24HOC | Non-Inverter | 2 | 1.83 | 22000 | 1800 | 12.2222 | 16800 | 2200 | 7.6364 | 9.92 | Split_Wall_Mounted AUX 1.83TR SEER 9.92 | Split_Wall_Mounted LG 1.74TR SEER 9.84
360 | Split_Wall_Mounted | LG | S182DP | Non-Inverter | 1.5 | 1.5 | 18000 | 1950 | 9.2308 | 16787.7386 | 2080 | 8.071 | 8.32 | Split_Wall_Mounted LG 1.5TR SEER 8.32 | Split_Wall_Mounted LG 1.53TR SEER 8.30
361 | Split_Wall_Mounted | Daikin | RY24HEVLK | Non-Inverter | 2 | 1.77 | 21350 | 2470 | 8.6437 | 18330 | 2770 | 6.6173 | 7.48 | Split_Wall_Mounted Daikin 1.77TR SEER 7.48 | Split_Wall_Mounted Daikin 1.78TR SEER 7.47
362 | Split_Wall_Mounted | LG | S242DP | Non-Inverter | 2 | 2 | 24000 | 2350 | 10.2128 | 18664 | 2840 | 6.5718 | 8.37 | Split_Wall_Mounted LG 2TR SEER 8.37 | Split_Wall_Mounted Carrier 2TR SEER 8.60
363 | Split_Wall_Mounted | LG | S242KO | Non-Inverter | 2 | 2 | 24000 | 2890 | 8.3045 | 19722 | 3200 | 6.1631 | 7.1 | Split_Wall_Mounted LG 2TR SEER 7.1 | Split_Wall_Mounted MITSUBISHI 2.03TR SEER 7.10
364 | Split_Wall_Mounted | LG | S182HN52 | Non-Inverter | 1.5 | 1.41 | 17026 | 2100 | 8.1076 | 14672 | 2450 | 5.9886 | 6.95 | Split_Wall_Mounted LG 1.41TR SEER 6.95 | Split_Wall_Mounted LG 1.54TR SEER 8.14
365 | Split_Wall_Mounted | Fuji | FOJ24SCH | Non-Inverter | 2 | 1.68 | 20200 | 1750 | 11.5429 | 17700 | 2130 | 8.3099 | 9.84 | Split_Wall_Mounted Fuji 1.68TR SEER 9.84 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
366 | Split_Wall_Mounted | Classic | AD030CHXCW2 | Non-Inverter | 2 | 2.29 | 27552.1368 | 2320 | 11.8759 | 24198 | 2847 | 8.4995 | 10.11 | Split_Wall_Mounted Classic 2.29TR SEER 10.11 | Split_Wall_Mounted GREE 2.19TR SEER 10.05
367 | Split_Wall_Mounted | Classic | KRC18CDMHJOW1 | Non-Inverter | 1.5 | 1.48 | 17777.7778 | 1532 | 11.6043 | 14781 | 1782 | 8.2946 | 9.83 | Split_Wall_Mounted Classic 1.48TR SEER 9.83 | Split_Wall_Mounted York 1.42TR SEER 9.83
368 | Split_Wall_Mounted | Classic | AD024CCXOW2 | Non-Inverter | 2 | 2.29 | 27500 | 2320 | 11.8534 | 24200 | 2847 | 8.5002 | 10.1 | Split_Wall_Mounted Classic 2.29TR SEER 10.1 | Split_Wall_Mounted GREE 2.19TR SEER 10.05
369 | Split_Wall_Mounted | Classic | AD018CCXOW | Non-Inverter | 1.5 | 1.5 | 18000 | 1558 | 11.5533 | 15000 | 1807 | 8.3011 | 9.8 | Split_Wall_Mounted Classic 1.5TR SEER 9.8 | Split_Wall_Mounted LG 1.46TR SEER 9.8
370 | Split_Wall_Mounted | Classic | AD024CHXOW2 | Non-Inverter | 2 | 1.91 | 23000 | 1965 | 11.7048 | 18300 | 2179 | 8.3983 | 9.89 | Split_Wall_Mounted Classic 1.91TR SEER 9.89 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
371 | Split_Wall_Mounted | Mando | KT3FR-61GWS | Non-Inverter | 1.5 | 1.47 | 17700 | 1740 | 10.1724 | 17700 | 2130 | 8.3099 | 9.08 | Split_Wall_Mounted Mando 1.47TR SEER 9.08 | Split_Wall_Mounted General 1.5TR SEER 10.16
372 | Split_Wall_Mounted | Mando | S-030-H/S | Non-Inverter | 2 | 2 | 24000 | 2080 | 11.5385 | 20500 | 2380 | 8.6134 | 9.91 | Split_Wall_Mounted Mando 2TR SEER 9.91 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
373 | Split_Wall_Mounted | LG | S12DDC | Non-Inverter | 1 | 1 | 12010 | 1200 | 10.0083 | 10577 | 1400 | 7.555 | 8.64 | Split_Wall_Mounted LG 1TR SEER 8.64 | Split_Wall_Mounted LG 0.95TR SEER 8.3
374 | Split_Wall_Mounted | LG | T3224HNV0 | Non-Inverter | 2.5 | 2.33 | 27979 | 2320 | 12.0599 | 24601 | 2650 | 9.2834 | 10.47 | Split_Wall_Mounted LG 2.33TR SEER 10.47 | Split_Wall_Mounted LG 2.33TR SEER 10.46
375 | Split_Wall_Mounted | Carrier | 42XPL030H3P | Non-Inverter | 2 | 2.25 | 27000 | 2260 | 11.9469 | 24000 | 2700 | 8.8889 | 10.29 | Split_Wall_Mounted Carrier 2.25TR SEER 10.29 | Split_Wall_Mounted Zamil 2.24TR SEER 10.35
376 | Split_Wall_Mounted | York | YJGE24XH3CHL-R5 | Non-Inverter | 2 | 1.83 | 22000 | 1810 | 12.1547 | 19000 | 2222 | 8.5509 | 10.28 | Split_Wall_Mounted York 1.83TR SEER 10.28 | Split_Wall_Mounted Mando 1.84TR SEER 10.28
377 | Split_Wall_Mounted | York | YJGE18XH3CHL | Non-Inverter | 1.5 | 1.5 | 18000 | 1481 | 12.154 | 15400 | 1800 | 8.5556 | 10.28 | Split_Wall_Mounted York 1.5TR SEER 10.28 | Split_Wall_Mounted Cooline 1.5TR SEER 10.25
378 | Split_Wall_Mounted | LG | LS-H242TG | Non-Inverter | 2 | 2 | 24000 | 2525 | 9.505 | 19142 | 2730 | 7.0117 | 8.1 | Split_Wall_Mounted LG 2TR SEER 8.1 | Split_Wall_Mounted Zamil 2.12TR SEER 8.09
379 | Split_Wall_Mounted | Samsung | AR24KRFHRWKN | Non-Inverter | 1.5 | 1.66 | 20000 | 1690 | 11.8343 | 16500 | 1950 | 8.4615 | 10.02 | Split_Wall_Mounted Samsung 1.66TR SEER 10.02 | Split_Wall_Mounted GREE 1.5TR SEER 9.98
380 | Split_Wall_Mounted | Midea | MSTE18CRNAB4 | Non-Inverter | 1.5 | 1.5 | 18000 | 1488 | 12.0968 | 15900 | 1849 | 8.5992 | 10.28 | Split_Wall_Mounted Midea 1.5TR SEER 10.28 | Split_Wall_Mounted Cooline 1.5TR SEER 10.25
381 | Split_Wall_Mounted | Fuji | FOJ24CO | Non-Inverter | 2 | 1.73 | 20704 | 2160 | 9.5852 | 17683 | 2390 | 7.3987 | 8.31 | Split_Wall_Mounted Fuji 1.73TR SEER 8.31 | Split_Wall_Mounted Carrier 1.79TR SEER 8.31
382 | Split_Wall_Mounted | Haier | HSU-18LZ413 | Non-Inverter | 1.5 | 1.43 | 17200 | 1450 | 11.8621 | 15000 | 1720 | 8.7209 | 10.16 | Split_Wall_Mounted Haier 1.43TR SEER 10.16 | Split_Wall_Mounted General 1.5TR SEER 10.16
383 | Split_Wall_Mounted | Carrier | 42HL0183P | Non-Inverter | 1.5 | 1.45 | 17500 | 1500 | 11.6667 | 15000 | 1780 | 8.427 | 9.94 | Split_Wall_Mounted Carrier 1.45TR SEER 9.94 | Split_Wall_Mounted Chigo 1.38TR SEER 9.88
384 | Split_Wall_Mounted | Matco | MATSF18H | Non-Inverter | 1.5 | 1.43 | 17197 | 1431 | 12.0175 | 14899 | 1703 | 8.7487 | 10.27 | Split_Wall_Mounted Matco 1.43TR SEER 10.27 | Split_Wall_Mounted Cooline 1.5TR SEER 10.25
385 | Split_Wall_Mounted | LG | B1824H | Non-Inverter | 1.5 | 1.45 | 17403 | 1510 | 11.5252 | 14978 | 1800 | 8.3211 | 9.82 | Split_Wall_Mounted LG 1.45TR SEER 9.82 | Split_Wall_Mounted LG 1.46TR SEER 9.8
386 | Split_Wall_Mounted | TACHIAIR | TC24H/6S15 | Non-Inverter | 2 | 1.68 | 20200 | 1750 | 11.5429 | 17700 | 2130 | 8.3099 | 9.84 | Split_Wall_Mounted TACHIAIR 1.68TR SEER 9.84 | Split_Wall_Mounted LG 1.74TR SEER 9.84
387 | Split_Wall_Mounted | Ugine | UGN- P24H-R | Non-Inverter | 2 | 1.93 | 23202 | 2000 | 11.601 | 19899 | 2390 | 8.3259 | 9.86 | Split_Wall_Mounted Ugine 1.93TR SEER 9.86 | Split_Wall_Mounted LG 1.74TR SEER 9.84
388 | Split_Wall_Mounted | LG | S182KC | Non-Inverter | 1.5 | 1.5 | 18000 | 1900 | 9.4737 | 13074 | 1940 | 6.7392 | 7.94 | Split_Wall_Mounted LG 1.5TR SEER 7.94 | Split_Wall_Mounted LG 1.54TR SEER 8.14
389 | Split_Wall_Mounted | LG | S122SH | Non-Inverter | 1 | 0.96 | 11480 | 1200 | 9.5667 | 10236 | 1400 | 7.3114 | 8.3 | Split_Wall_Mounted LG 0.96TR SEER 8.3 | Split_Wall_Mounted LG 0.95TR SEER 8.3
390 | Split_Wall_Mounted | LG | LS-H242TM | Non-Inverter | 2 | 2 | 24000 | 2525 | 9.505 | 19143 | 2730 | 7.0121 | 8.1 | Split_Wall_Mounted LG 2TR SEER 8.1 | Split_Wall_Mounted Zamil 2.12TR SEER 8.09
391 | Split_Wall_Mounted | LG | B182PH | Non-Inverter | 1.5 | 1.45 | 17469 | 1510 | 11.5689 | 14979 | 1800 | 8.3217 | 9.84 | Split_Wall_Mounted LG 1.45TR SEER 9.84 | Split_Wall_Mounted LG 1.45TR SEER 9.84
392 | Split_Wall_Mounted | LG | B242PH | Non-Inverter | 2 | 1.74 | 20886 | 1820 | 11.4758 | 19941 | 2280 | 8.7461 | 10.01 | Split_Wall_Mounted LG 1.74TR SEER 10.01 | Split_Wall_Mounted Carrier 1.83TR SEER 10.08
393 | Split_Wall_Mounted | Haam | HM36C | Non-Inverter | 2 | 2.3 | 27600 | 2400 | 11.5 | 23500 | 2880 | 8.1597 | 9.74 | Split_Wall_Mounted Haam 2.3TR SEER 9.74 | Split_Wall_Mounted Samsung 2.33TR SEER 9.83
394 | Split_Wall_Mounted | Dansat | DSA18C | Non-Inverter | 1.5 | 1.44 | 17300 | 1430 | 12.0979 | 14900 | 1710 | 8.7135 | 10.3 | Split_Wall_Mounted Dansat 1.44TR SEER 10.3 | Split_Wall_Mounted Cooline 1.5TR SEER 10.25
395 | Split_Wall_Mounted | York | YHQE24XT2CHS | Non-Inverter | 2 | 1.83 | 22000 | 1774 | 12.4014 | 19000 | 2183 | 8.7036 | 10.49 | Split_Wall_Mounted York 1.83TR SEER 10.49 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
396 | Split_Wall_Mounted | Classic | AD018CCXOD | Non-Inverter | 1.5 | 1.51 | 18196 | 1389 | 13.1001 | 15502 | 1722 | 9.0023 | 11 | Split_Wall_Mounted Classic 1.51TR SEER 11 | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
397 | Split_Wall_Mounted | Aukia | AUK24CH | Non-Inverter | 2 | 1.8 | 21666 | 1830 | 11.8393 | 18766 | 2200 | 8.53 | 10.08 | Split_Wall_Mounted Aukia 1.8TR SEER 10.08 | Split_Wall_Mounted Carrier 1.83TR SEER 10.08
398 | Split_Wall_Mounted | LG | LS-H242TLB1 | Non-Inverter | 2 | 1.79 | 21496 | 2700 | 7.9615 | 18425 | 3250 | 5.6692 | 6.76 | Split_Wall_Mounted LG 1.79TR SEER 6.76 | Split_Wall_Mounted Zamil 2TR SEER 6.69
399 | Split_Wall_Mounted | Carrier | 42QKB0363P | Non-Inverter | 2.5 | 2.61 | 31400 | 2595 | 12.1002 | 26600 | 3093 | 8.6001 | 10.25 | Split_Wall_Mounted Carrier 2.61TR SEER 10.25 | Split_Wall_Mounted Carrier 2.58TR SEER 10.41
400 | Split_Wall_Mounted | Carrier | 42QKA0183P | Non-Inverter | 1.5 | 1.45 | 17500 | 1434 | 12.2036 | 15500 | 1761 | 8.8018 | 10.42 | Split_Wall_Mounted Carrier 1.45TR SEER 10.42 | Split_Wall_Mounted Mando 1.53TR SEER 10.38
401 | Split_Wall_Mounted | Carrier | 42QHL0243P | Non-Inverter | 2 | 1.79 | 21500 | 1800 | 11.9444 | 18500 | 2130 | 8.6854 | 10.19 | Split_Wall_Mounted Carrier 1.79TR SEER 10.19 | Split_Wall_Mounted Gree 1.83TR SEER 10.17
402 | Split_Wall_Mounted | Carrier | 38QHL0183 | Non-Inverter | 1.5 | 1.45 | 17500 | 1500 | 11.6667 | 15000 | 1780 | 8.427 | 9.94 | Split_Wall_Mounted Carrier 1.45TR SEER 9.94 | Split_Wall_Mounted Chigo 1.38TR SEER 9.88
403 | Split_Wall_Mounted | Hitachi | RMB018ABDA4EZ1 | Non-Inverter | 1.5 | 1.48 | 17800 | 1460 | 12.1918 | 14900 | 1760 | 8.4659 | 10.25 | Split_Wall_Mounted Hitachi 1.48TR SEER 10.25 | Split_Wall_Mounted Cooline 1.5TR SEER 10.25
404 | Split_Wall_Mounted | Beko | BTYSH240 | Non-Inverter | 2 | 1.7 | 20500 | 2503 | 8.1902 | 19107 | 3000 | 6.369 | 7.17 | Split_Wall_Mounted Beko 1.7TR SEER 7.17 | Split_Wall_Mounted LG 1.87TR SEER 7.14
405 | Split_Wall_Mounted | Gree | GWC24ACE | Non-Inverter | 2 | 1.83 | 22000 | 1880 | 11.7021 | 18700 | 2255 | 8.2927 | 9.91 | Split_Wall_Mounted Gree 1.83TR SEER 9.91 | Split_Wall_Mounted LG 1.74TR SEER 9.84
406 | Split_Wall_Mounted | Gree | GAN24C | Non-Inverter | 2 | 1.76 | 21200 | 1730 | 12.2543 | 18500 | 2050 | 9.0244 | 10.51 | Split_Wall_Mounted Gree 1.76TR SEER 10.51 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
407 | Split_Wall_Mounted | LG | S182MH | Non-Inverter | 1.5 | 1.5 | 18017.094 | 2060 | 8.7462 | 15491 | 2370 | 6.5363 | 7.52 | Split_Wall_Mounted LG 1.5TR SEER 7.52 | Split_Wall_Mounted LG 1.46TR SEER 7.56
408 | Split_Wall_Mounted | Kelvinator | KMS18H8 | Non-Inverter | 1.5 | 1.5 | 18100 | 1484 | 12.1968 | 15900 | 1797 | 8.8481 | 10.42 | Split_Wall_Mounted Kelvinator 1.5TR SEER 10.42 | Split_Wall_Mounted Mando 1.53TR SEER 10.38
409 | Split_Wall_Mounted | LG | S-242SH | Non-Inverter | 2 | 1.88 | 22598.2906 | 2640 | 8.56 | 18937 | 3250 | 5.8268 | 7.16 | Split_Wall_Mounted LG 1.88TR SEER 7.16 | Split_Wall_Mounted LG 1.87TR SEER 7.14
410 | Split_Wall_Mounted | Midea | MSTM18CRN | Non-Inverter | 1.5 | 1.55 | 18660 | 1545 | 12.0777 | 16282 | 1850 | 8.8011 | 10.33 | Split_Wall_Mounted Midea 1.55TR SEER 10.33 | Split_Wall_Mounted Mando 1.5TR SEER 10.35
411 | Split_Wall_Mounted | Gree | GWH30ACE-D3NTA1D-/O | Non-Inverter | 2 | 2.27 | 27300 | 2310 | 11.8182 | 23000 | 2705 | 8.5028 | 10.04 | Split_Wall_Mounted Gree 2.27TR SEER 10.04 | Split_Wall_Mounted GREE 2.19TR SEER 10.05
412 | Split_Wall_Mounted | Gree | GWH18ACD-D3NTA1F/O | Non-Inverter | 1.5 | 1.5 | 18000 | 1525 | 11.8033 | 14900 | 1773 | 8.4038 | 9.99 | Split_Wall_Mounted Gree 1.5TR SEER 9.99 | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
413 | Split_Wall_Mounted | KAYAN | KAYANN-ENERGY-1975-18K-H | Non-Inverter | 1.5 | 1.45 | 17400 | 1510 | 11.5232 | 14900 | 1730 | 8.6127 | 9.9 | Split_Wall_Mounted KAYAN 1.45TR SEER 9.9 | Split_Wall_Mounted Chigo 1.38TR SEER 9.88
414 | Split_Wall_Mounted | Gree | GWC24QE-D3NTBF/O | Non-Inverter | 2 | 1.83 | 22000 | 1880 | 11.7021 | 18700 | 2255 | 8.2927 | 9.91 | Split_Wall_Mounted Gree 1.83TR SEER 9.91 | Split_Wall_Mounted LG 1.74TR SEER 9.84
415 | Split_Wall_Mounted | Gree | GWC18ACD-D3NTA1H/O | Non-Inverter | 1.5 | 1.5 | 18000 | 1525 | 11.8033 | 14900 | 1773 | 8.4038 | 9.99 | Split_Wall_Mounted Gree 1.5TR SEER 9.99 | Split_Wall_Mounted GREE 1.5TR SEER 9.98
416 | Split_Wall_Mounted | Gree | GWH36LB-D3NTB2A/O | Non-Inverter | 2.5 | 2.5 | 30000 | 2540 | 11.811 | 25200 | 2960 | 8.5135 | 10.04 | Split_Wall_Mounted Gree 2.5TR SEER 10.04 | Split_Wall_Mounted LG 2.5TR SEER 10.43
417 | Split_Wall_Mounted | Haam | HM12CWM7S17 | Non-Inverter | 1 | 0.99 | 11900 | 1000 | 11.9 | 10300 | 1190 | 8.6555 | 10.16 | Split_Wall_Mounted Haam 0.99TR SEER 10.16 | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
418 | Split_Wall_Mounted | Gree | GWH18ACD-D3NTA1F/I | Non-Inverter | 1.5 | 1.5 | 18000 | 1525 | 11.8033 | 14900 | 1773 | 8.4038 | 9.99 | Split_Wall_Mounted Gree 1.5TR SEER 9.99 | Split_Wall_Mounted GREE 1.5TR SEER 9.98
419 | Split_Wall_Mounted | Falcon | FMS18H9 | Non-Inverter | 1.5 | 1.5 | 18000 | 1452 | 12.3967 | 15900 | 1797 | 8.8481 | 10.55 | Split_Wall_Mounted Falcon 1.5TR SEER 10.55 | Split_Wall_Mounted Zamil 1.49TR SEER 10.52
420 | Split_Wall_Mounted | Gree | GWH24ACE-D3NTA1B/O | Non-Inverter | 2 | 1.84 | 22100 | 1840 | 12.0109 | 19100 | 2213 | 8.6308 | 10.22 | Split_Wall_Mounted Gree 1.84TR SEER 10.22 | Split_Wall_Mounted LG 1.83TR SEER 10.27
421 | Split_Wall_Mounted | Haam | HM36C/8816 | Non-Inverter | 2 | 2.3 | 27600 | 2400 | 11.5 | 23500 | 2880 | 8.1597 | 9.74 | Split_Wall_Mounted Haam 2.3TR SEER 9.74 | Split_Wall_Mounted Samsung 2.33TR SEER 9.83
422 | Split_Wall_Mounted | Gree | GWH30ACE-D3NTA1D/O | Non-Inverter | 2 | 2.27 | 27300 | 2310 | 11.8182 | 23000 | 2705 | 8.5028 | 10.04 | Split_Wall_Mounted Gree 2.27TR SEER 10.04 | Split_Wall_Mounted GREE 2.19TR SEER 10.05
423 | Split_Wall_Mounted | Gree | GWH18QD-D3NTA1E/O | Non-Inverter | 1.5 | 1.5 | 18000 | 1525 | 11.8033 | 14900 | 1773 | 8.4038 | 9.99 | Split_Wall_Mounted Gree 1.5TR SEER 9.99 | Split_Wall_Mounted GREE 1.5TR SEER 9.98
424 | Split_Wall_Mounted | YOKO | YOKO-30CH | Non-Inverter | 2 | 2.18 | 26170 | 2200 | 11.8955 | 22174 | 2671 | 8.3018 | 10.03 | Split_Wall_Mounted YOKO 2.18TR SEER 10.03 | Split_Wall_Mounted GREE 2.19TR SEER 10.05
425 | Split_Wall_Mounted | Falcon | FMS30H9 | Non-Inverter | 2 | 2.25 | 27000 | 2180 | 12.3853 | 23800 | 2645 | 8.9981 | 10.59 | Split_Wall_Mounted Falcon 2.25TR SEER 10.59 | Split_Wall_Mounted Gree 2.25TR SEER 11.11
426 | Split_Wall_Mounted | Haam | KFR-61GW/a | Non-Inverter | 2 | 1.73 | 20814.064 | 2320 | 8.9716 | 17743 | 2650 | 6.6955 | 7.71 | Split_Wall_Mounted Haam 1.73TR SEER 7.71 | Split_Wall_Mounted Carrier 1.75TR SEER 7.63
427 | Split_Wall_Mounted | General | GNPL24HHL | Non-Inverter | 2 | 1.75 | 21000 | 1700 | 12.3529 | 18100 | 2070 | 8.744 | 10.47 | Split_Wall_Mounted General 1.75TR SEER 10.47 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
428 | Split_Wall_Mounted | LG | B2427H | Non-Inverter | 2 | 1.74 | 20950 | 1820 | 11.511 | 18937 | 2280 | 8.3057 | 9.84 | Split_Wall_Mounted LG 1.74TR SEER 9.84 | Split_Wall_Mounted LG 1.74TR SEER 9.84
429 | Split_Wall_Mounted | Daewoo | DS4-24W | Non-Inverter | 2 | 2 | 24000 | 2320 | 10.3448 | 20000 | 2750 | 7.2727 | 8.73 | Split_Wall_Mounted Daewoo 2TR SEER 8.73 | Split_Wall_Mounted Carrier 2TR SEER 8.60
430 | Split_Wall_Mounted | Falcon | FTS36C | Non-Inverter | 2.5 | 2.4 | 28860 | 2306 | 12.5152 | 23600 | 2713 | 8.6989 | 10.51 | Split_Wall_Mounted Falcon 2.4TR SEER 10.51 | Split_Wall_Mounted Carrier 2.58TR SEER 10.41
431 | Split_Wall_Mounted | York | YHGE24YT2BFEO-3 | Non-Inverter | 2 | 1.91 | 23000 | 1870 | 12.2995 | 19800 | 2275 | 8.7033 | 10.42 | Split_Wall_Mounted York 1.91TR SEER 10.42 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
432 | Split_Wall_Mounted | Mando | S-D30H/HR | Non-Inverter | 2 | 1.99 | 23884.99 | 2000 | 11.9425 | 21496 | 3200 | 6.7175 | 9.47 | Split_Wall_Mounted Mando 1.99TR SEER 9.47 | Split_Wall_Mounted Zamil 1.99TR SEER9.77
433 | Split_Wall_Mounted | Craft | DS24CE7SCWT | Non-Inverter | 2 | 2 | 24000 | 1846 | 13.0011 | 20400 | 2400 | 8.5 | 10.76 | Split_Wall_Mounted Craft 2TR SEER 10.76 | Split_Wall_Mounted Zamil 2TR SEER 10.39
434 | Split_Wall_Mounted | Gree | GWH18ACD-D3NTA1H/I | Non-Inverter | 1.5 | 1.5 | 18000 | 1525 | 11.8033 | 14900 | 1773 | 8.4038 | 9.99 | Split_Wall_Mounted Gree 1.5TR SEER 9.99 | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
435 | Split_Wall_Mounted | Gree | GWH18QD-D3NTB4D/I | Non-Inverter | 1.5 | 1.5 | 18000 | 1525 | 11.8033 | 14900 | 1773 | 8.4038 | 9.99 | Split_Wall_Mounted Gree 1.5TR SEER 9.99 | Split_Wall_Mounted GREE 1.5TR SEER 9.98
436 | Split_Wall_Mounted | LG | T242EH | Non-Inverter | 2 | 1.87 | 22520 | 2650 | 8.4981 | 19619 | 3080 | 6.3698 | 7.32 | Split_Wall_Mounted LG 1.87TR SEER 7.32 | Split_Wall_Mounted LG 1.79TR SEER 7.34
437 | Split_Wall_Mounted | Gree | GW24QE-D3NTB4F/I | Non-Inverter | 2 | 1.84 | 22100 | 1880 | 11.7553 | 18700 | 2255 | 8.2927 | 9.94 | Split_Wall_Mounted Gree 1.84TR SEER 9.94 | Split_Wall_Mounted LG 1.74TR SEER 9.84
438 | Split_Wall_Mounted | Gree | GWH36LB-D3NTB2A/I | Non-Inverter | 2.5 | 2.5 | 30000 | 2540 | 11.811 | 25200 | 2960 | 8.5135 | 10.04 | Split_Wall_Mounted Gree 2.5TR SEER 10.04 | Split_Wall_Mounted LG 2.5TR SEER 10.43
439 | Split_Wall_Mounted | Gree | GWH36QE-D3NTB4A/I | Non-Inverter | 2 | 2.19 | 26300 | 2230 | 11.7937 | 22800 | 2680 | 8.5075 | 10.05 | Split_Wall_Mounted Gree 2.19TR SEER 10.05 | Split_Wall_Mounted GREE 2.19TR SEER 10.05
440 | Split_Wall_Mounted | Gree | GWC24AGEXF-D3NTA1C/I | Non-Inverter | 2 | 1.83 | 22200 | 1818 | 12.2112 | 19400 | 2194 | 8.8423 | 10.42 | Split_Wall_Mounted Gree 1.83TR SEER 10.42 | Split_Wall_Mounted Zamil 1.83TR SEER 10.42
441 | Split_Wall_Mounted | TACHIAIR | TC18H/7S16 | Non-Inverter | 1.5 | 1.45 | 17400 | 1510 | 11.5232 | 14900 | 1730 | 8.6127 | 9.9 | Split_Wall_Mounted TACHIAIR 1.45TR SEER 9.9 | Split_Wall_Mounted Chigo 1.38TR SEER 9.88
442 | Split_Wall_Mounted | WBOX | WBAC24HL | Non-Inverter | 2 | 1.75 | 21000 | 1730 | 12.1387 | 18600 | 2130 | 8.7324 | 10.35 | Split_Wall_Mounted WBOX 1.75TR SEER 10.35 | Split_Wall_Mounted Carrier 1.79TR SEER 10.35
443 | Split_Wall_Mounted | Unix | 18TCS | Non-Inverter | 1.5 | 1.5 | 18000 | 1500 | 12 | 16100 | 1894 | 8.5005 | 10.2 | Split_Wall_Mounted Unix 1.5TR SEER 10.2 | Split_Wall_Mounted General 1.5TR SEER 10.16
444 | Split_Wall_Mounted | Ugine | UASM36C | Non-Inverter | 2.5 | 2.61 | 31400 | 2614 | 12.0122 | 26800 | 3135 | 8.5486 | 10.19 | Split_Wall_Mounted Ugine 2.61TR SEER 10.19 | Split_Wall_Mounted Zamil 2.62TR SEER 10.00
445 | Split_Wall_Mounted | Carrier | 42XP090H3 | Non-Inverter | 2.5 | 2.37 | 28551 | 3160 | 9.0351 | 24500 | 3398 | 7.2101 | 7.9 | Split_Wall_Mounted Carrier 2.37TR SEER 7.9 | Split_Wall_Mounted Zamil 2.35TR SEER 9.85
446 | Split_Wall_Mounted | LG | LV-H362KLA3 | Non-Inverter | 3 | 2.92 | 35145 | 3600 | 9.7625 | 29685 | 4200 | 7.0679 | 8.31 | Split_Wall_Mounted LG 2.92TR SEER 8.31 | Split_Wall_Mounted Carrier 2.75TR SEER 8.54
447 | Split_Wall_Mounted | Haier | HSY-18EA13(T3) | Non-Inverter | 1.5 | 1.42 | 17100 | 1900 | 9 | 14700 | 2300 | 6.3913 | 7.63 | Split_Wall_Mounted Haier 1.42TR SEER 7.63 | Split_Wall_Mounted Royal Temp 1.5TR SEER 7.67
448 | Split_Wall_Mounted | YONAN | KT3FR-24GW/X1a | Non-Inverter | 2 | 2 | 24450 | 2054 | 11.9036 | 20950 | 2464 | 8.5024 | 10.11 | Split_Wall_Mounted YONAN 2TR SEER 10.11 | Split_Wall_Mounted GREE 2.19TR SEER 10.05
449 | Split_Wall_Mounted | Zamil | MAZ26CCXAD | Non-Inverter | 2 | 1.99 | 23953 | 1832 | 13.0748 | 20745 | 2278 | 9.1067 | 11.03 | Split_Wall_Mounted Zamil 1.99TR SEER 11.03 | Split_Wall_Mounted Zamil 2TR SEER 10.39
450 | Split_Wall_Mounted | LG | S182SC | Non-Inverter | 1.5 | 1.45 | 17504 | 2000 | 8.752 | 15354 | 2300 | 6.6757 | 7.58 | Split_Wall_Mounted LG 1.45TR SEER 7.58 | Split_Wall_Mounted Cooline 1.5TR SEER 10.25
451 | Split_Wall_Mounted | Zamil | MAZ26CCXAD1 | Non-Inverter | 2 | 1.83 | 22000 | 1781 | 12.3526 | 18398 | 2114 | 8.7029 | 10.43 | Split_Wall_Mounted Zamil 1.83TR SEER 10.43 | Split_Wall_Mounted Zamil 1.83TR SEER 10.42
452 | Split_Wall_Mounted | STARWAY | STW 24K CR | Non-Inverter | 2 | 1.9 | 22800 | 1880 | 12.1277 | 19220 | 2210 | 8.6968 | 10.3 | Split_Wall_Mounted STARWAY 1.9TR SEER 10.3 | Split_Wall_Mounted Mando 1.84TR SEER 10.28
453 | Split_Wall_Mounted | Gree | GWH24ACE-D3NTA1C/I | Non-Inverter | 2 | 1.83 | 22000 | 1865 | 11.7962 | 18300 | 2200 | 8.3182 | 9.96 | Split_Wall_Mounted Gree 1.83TR SEER 9.96 | Split_Wall_Mounted LG 1.74TR SEER 9.84
454 | Split_Wall_Mounted | Mando | M20T-18C | Non-Inverter | 1.5 | 1.53 | 18400 | 1484 | 12.3989 | 16200 | 1800 | 9 | 10.6 | Split_Wall_Mounted Mando 1.53TR SEER 10.6 | Split_Wall_Mounted Zamil 1.49TR SEER 10.52
455 | Split_Wall_Mounted | LG | T3224C | Inverter | 2.5 | 2.34 | 28184 | 2240 | 12.5821 | 22383 | 2516 | 8.8963 | 10.59 | Split_Wall_Mounted LG 2.34TR SEER 10.59 | Inverter unit "No replacement"
456 | Split_Wall_Mounted | Samsung | AR24JRFNCWKN | Non-Inverter | 1.5 | 1.66 | 20000 | 1600 | 12.5 | 16500 | 1900 | 8.6842 | 10.5 | Split_Wall_Mounted Samsung 1.66TR SEER 10.5 | Split_Wall_Mounted Zamil 1.49TR SEER 10.52
457 | Split_Wall_Mounted | Mando | AC-MD-24H-FW | Non-Inverter | 2 | 1.71 | 20545 | 1739 | 11.8143 | 17577 | 2105 | 8.3501 | 10 | Split_Wall_Mounted Mando 1.71TR SEER 10 | Split_Wall_Mounted Carrier 1.83TR SEER 10.08
458 | Split_Wall_Mounted | Mando | KFR-51QW/a | Non-Inverter | 1.5 | 1.45 | 17400 | 1810 | 9.6133 | 14300 | 1960 | 7.2959 | 8.27 | Split_Wall_Mounted Mando 1.45TR SEER 8.27 | Split_Wall_Mounted LG 1.53TR SEER 8.30
459 | Split_Wall_Mounted | Daewoo | DSA-183LH | Non-Inverter | 1.5 | 1.5 | 18000 | 2000 | 9 | 15200 | 2300 | 6.6087 | 7.69 | Split_Wall_Mounted Daewoo 1.5TR SEER 7.69 | Split_Wall_Mounted Royal Temp 1.5TR SEER 7.67
460 | Split_Wall_Mounted | Mando | S-030H/hr | Non-Inverter | 2.5 | 2.5 | 30000 | 2800 | 10.7143 | 27000 | 3200 | 8.4375 | 9.37 | Split_Wall_Mounted Mando 2.5TR SEER 9.37 | Split_Wall_Mounted LG 2.58TR SEER 9.72
461 | Split_Wall_Mounted | LG | S242NHU52 | Non-Inverter | 2 | 1.83 | 22000 | 2640 | 8.3333 | 18920 | 3250 | 5.8215 | 7.04 | Split_Wall_Mounted LG 1.83TR SEER 7.04 | Split_Wall_Mounted Zamil 1.99TR SEER9.77
462 | Split_Wall_Mounted | Mando | KT3FR-81W/S | Non-Inverter | 2 | 1.68 | 20200 | 1750 | 11.5429 | 17700 | 2130 | 8.3099 | 9.84 | Split_Wall_Mounted Mando 1.68TR SEER 9.84 | Split_Wall_Mounted LG 1.74TR SEER 9.84
463 | Split_Wall_Mounted | SKM | MSKM410A-24HEP8 | Non-Inverter | 2 | 1.83 | 22000 | 1803 | 12.2019 | 18500 | 2164 | 8.549 | 10.29 | Split_Wall_Mounted SKM 1.83TR SEER 10.29 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
464 | Split_Wall_Mounted | SKM | MSKM410A-18CEP8 | Non-Inverter | 1.5 | 1.5 | 18000 | 1488 | 12.0968 | 15900 | 1849 | 8.5992 | 10.28 | Split_Wall_Mounted SKM 1.5TR SEER 10.28 | Split_Wall_Mounted Cooline 1.5TR SEER 10.25
465 | Split_Wall_Mounted | York | YJGE24YH3CHLO-5 | Non-Inverter | 2 | 1.83 | 22000 | 1818 | 12.1012 | 19000 | 2223 | 8.547 | 10.25 | Split_Wall_Mounted York 1.83TR SEER 10.25 | Split_Wall_Mounted LG 1.83TR SEER 10.27
466 | Split_Wall_Mounted | Ugine | UASM24H | Non-Inverter | 2 | 1.83 | 22000 | 1781 | 12.3526 | 18400 | 2114 | 8.7039 | 10.43 | Split_Wall_Mounted Ugine 1.83TR SEER 10.43 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
467 | Split_Wall_Mounted | Haam | HM30HSM22GO | Non-Inverter | 2 | 2.25 | 27000 | 2180 | 12.3853 | 23800 | 2615 | 9.1013 | 10.62 | Split_Wall_Mounted Haam 2.25TR SEER 10.62 | Split_Wall_Mounted Okia 2.25TR SEER 10.59
468 | Split_Wall_Mounted | Zamil | TRL18CDACIED1 | Non-Inverter | 1.5 | 1.5 | 18000 | 1488 | 12.0968 | 15600 | 1814 | 8.5998 | 10.27 | Split_Wall_Mounted Zamil 1.5TR SEER 10.27 | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
469 | Split_Wall_Mounted | York | YHGE18YT3CFEO-4 | Non-Inverter | 1.5 | 1.5 | 18000 | 1450 | 12.4138 | 15300 | 1760 | 8.6932 | 10.48 | Split_Wall_Mounted York 1.5TR SEER 10.48 | Split_Wall_Mounted LG 1.5TR SEER 10.46
470 | Split_Wall_Mounted | RAVO | RV20T-24C | Non-Inverter | 2 | 1.75 | 21000 | 1750 | 12 | 18900 | 2100 | 9 | 10.36 | Split_Wall_Mounted RAVO 1.75TR SEER 10.36 | Split_Wall_Mounted Giant 1.75TR SEER 10.36
471 | Split_Wall_Mounted | Giant | GIANT-30C | Non-Inverter | 2 | 2.23 | 26800 | 2161 | 12.4017 | 22200 | 2552 | 8.6991 | 10.45 | Split_Wall_Mounted Giant 2.23TR SEER 10.45 | Split_Wall_Mounted LG 2.33TR SEER 10.46
472 | Split_Wall_Mounted | TIT | TIS-2420C | Non-Inverter | 2 | 1.83 | 22000 | 1775 | 12.3944 | 19000 | 2200 | 8.6364 | 10.46 | Split_Wall_Mounted TIT 1.83TR SEER 10.46 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
473 | Split_Wall_Mounted | General | GC-24KFC | Non-Inverter | 2 | 1.75 | 21000 | 1750 | 12 | 18900 | 2100 | 9 | 10.36 | Split_Wall_Mounted General 1.75TR SEER 10.36 | Split_Wall_Mounted Giant 1.75TR SEER 10.36
474 | Split_Wall_Mounted | Falcon | RGS24H | Non-Inverter | 2 | 2 | 24000 | 2630 | 9.1255 | 21508 | 3850 | 5.5865 | 7.43 | Split_Wall_Mounted Falcon 2TR SEER 7.43 | Split_Wall_Mounted Zamil 1.83TR SEER 7.51
475 | Split_Wall_Mounted | Dansat | DSH18C | Non-Inverter | 1.5 | 1.5 | 18000 | 1500 | 12 | 15000 | 1720 | 8.7209 | 10.21 | Split_Wall_Mounted Dansat 1.5TR SEER 10.21 | Split_Wall_Mounted Ugine 1.48TR SEER 10.23
476 | Split_Wall_Mounted | Gree | GWH24ACE-D3NTA1A/O | Non-Inverter | 2 | 1.83 | 22000 | 1880 | 11.7021 | 18300 | 2200 | 8.3182 | 9.9 | Split_Wall_Mounted Gree 1.83TR SEER 9.9 | Split_Wall_Mounted LG 1.74TR SEER 9.84
477 | Split_Wall_Mounted | GoldStar | Model 01GoldStar | Non-Inverter | 2 | 2 | 24000 | 2500 | 9.6 | 19600 | 3000 | 6.5333 | 8.02 | Split_Wall_Mounted GoldStar 2TR SEER 8.02 | Split_Wall_Mounted Zamil 2.12TR SEER 8.09
478 | Split_Wall_Mounted | QUEEN | HQSif20C | Non-Inverter | 1 | 1 | 12000 | 1000 | 12 | 10200 | 1200 | 8.5 | 10.16 | Split_Wall_Mounted QUEEN 1TR SEER 10.16 | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
479 | Split_Wall_Mounted | Smart_Electric | SMELE24C | Non-Inverter | 2 | 1.91 | 23000 | 1855 | 12.3989 | 19800 | 2275 | 8.7033 | 10.48 | Split_Wall_Mounted Smart_Electric 1.91TR SEER 10.48 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
480 | Split_Wall_Mounted | York | YHFE12XT3CFE-R3 | Non-Inverter | 1 | 0.99 | 11900 | 975 | 12.2051 | 10000 | 1150 | 8.6957 | 10.34 | Split_Wall_Mounted York 0.99TR SEER 10.34 | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
481 | Split_Wall_Mounted | Hisense | AS-18CTS | Non-Inverter | 1.5 | 1.5 | 18000 | 1485 | 12.1212 | 15600 | 1785 | 8.7395 | 10.33 | Split_Wall_Mounted Hisense 1.5TR SEER 10.33 | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
482 | Split_Wall_Mounted | LG | NV242C1 | Inverter | 1.5 | 1.66 | 20000 | 1613 | 12.3993 | 17000 | 1954 | 8.7001 | 10.47 | Split_Wall_Mounted LG 1.66TR SEER 10.47 | Inverter unit "No replacement"
483 | Split_Wall_Mounted | Haam | HM24C/7S15 | Non-Inverter | 2 | 1.73 | 20800 | 1800 | 11.5556 | 16700 | 2000 | 8.35 | 9.79 | Split_Wall_Mounted Haam 1.73TR SEER 9.79 | Split_Wall_Mounted LG 1.82TR SEER 9.79
484 | Split_Wall_Mounted | EMJOI | UESA-24C6 | Non-Inverter | 2 | 1.75 | 21040 | 1815 | 11.5923 | 17060 | 2055 | 8.3017 | 9.81 | Split_Wall_Mounted EMJOI 1.75TR SEER 9.81 | Split_Wall_Mounted LG 1.82TR SEER 9.79
485 | Split_Wall_Mounted | Carrier | 38QHA024HS | Non-Inverter | 2 | 1.79 | 21500 | 1780 | 12.0787 | 18400 | 2140 | 8.5981 | 10.25 | Split_Wall_Mounted Carrier 1.79TR SEER 10.25 | Split_Wall_Mounted LG 1.83TR SEER 10.27
486 | Split_Wall_Mounted | Zamil | MFZ24CHXFW | Non-Inverter | 2 | 1.83 | 22000 | 1905 | 11.5486 | 18500 | 2229 | 8.2997 | 9.81 | Split_Wall_Mounted Zamil 1.83TR SEER 9.81 | Split_Wall_Mounted LG 1.99TR SEER 9.80
487 | Split_Wall_Mounted | York | YK9FXC024BAH-AX | Non-Inverter | 2 | 1.83 | 22000 | 1850 | 11.8919 | 19500 | 2250 | 8.6667 | 10.18 | Split_Wall_Mounted York 1.83TR SEER 10.18 | Split_Wall_Mounted Gree 1.83TR SEER 10.17
488 | Split_Wall_Mounted | Mando | MP-SER-24C | Non-Inverter | 2 | 1.83 | 22000 | 1781 | 12.3526 | 18200 | 2128 | 8.5526 | 10.37 | Split_Wall_Mounted Mando 1.83TR SEER 10.37 | Split_Wall_Mounted Giant 1.75TR SEER 10.36
489 | Split_Wall_Mounted | Zamil | MFZ24CCXFW | Non-Inverter | 2 | 1.84 | 22100 | 1922 | 11.4984 | 19000 | 2289 | 8.3006 | 9.79 | Split_Wall_Mounted Zamil 1.84TR SEER 9.79 | Split_Wall_Mounted LG 1.82TR SEER 9.79
490 | Split_Wall_Mounted | Craft | DSA30CE6YHA1 | Non-Inverter | 2 | 2.25 | 27000 | 2230 | 12.1076 | 23200 | 2680 | 8.6567 | 10.29 | Split_Wall_Mounted Craft 2.25TR SEER 10.29 | Split_Wall_Mounted Zamil 2.24TR SEER 10.35
491 | Split_Wall_Mounted | LG | S322GC | Non-Inverter | 2 | 2.25 | 27000 | 3210 | 8.4112 | 23750 | 3690 | 6.4363 | 7.29 | Split_Wall_Mounted LG 2.25TR SEER 7.29 | Split_Wall_Mounted LG 2.25TR SEER 7.28
492 | Split_Wall_Mounted | Zamil | MMZ36CCXAD | Non-Inverter | 2.5 | 2.6 | 31300 | 2614 | 11.974 | 26900 | 3135 | 8.5805 | 10.18 | Split_Wall_Mounted Zamil 2.6TR SEER 10.18 | Split_Wall_Mounted Zamil 2.62TR SEER 10.00
493 | Split_Wall_Mounted | York | YHFE24YT3VFEO-3 / YHFE24XT3CFE-R3 | Non-Inverter | 2 | 1.91 | 23000 | 1870 | 12.2995 | 19800 | 2275 | 8.7033 | 10.42 | Split_Wall_Mounted York 1.91TR SEER 10.42 | Split_Wall_Mounted Zamil 1.83TR SEER 10.42
494 | Split_Wall_Mounted | York | YHGE24YT2BFEO-3 / YHGE24XT2BFE-R3 | Non-Inverter | 2 | 1.91 | 23000 | 1925 | 11.9481 | 19800 | 2290 | 8.6463 | 10.18 | Split_Wall_Mounted York 1.91TR SEER 10.18 | Split_Wall_Mounted Gree 1.83TR SEER 10.17
495 | Split_Wall_Mounted | York | YK9FYH024BAH-AAX / YK9FXH024BAH--AX | Non-Inverter | 2 | 1.83 | 22000 | 1850 | 11.8919 | 19500 | 2250 | 8.6667 | 10.18 | Split_Wall_Mounted York 1.83TR SEER 10.18 | Split_Wall_Mounted Gree 1.83TR SEER 10.17
496 | Split_Wall_Mounted | York | MP920-18H / MP920-18H | Non-Inverter | 1.5 | 1.5 | 18000 | 1452 | 12.3967 | 15900 | 1767 | 8.9983 | 10.6 | Split_Wall_Mounted York 1.5TR SEER 10.6 | Split_Wall_Mounted Zamil 1.49TR SEER 10.52
497 | Split_Wall_Mounted | York | YE5SD180SHZW22 / YE5HC18SH7BC22 | Non-Inverter | 1.5 | 1.41 | 17000 | 1783 | 9.5345 | 15141 | 2204 | 6.8698 | 8.14 | Split_Wall_Mounted York 1.41TR SEER 8.14 | Split_Wall_Mounted LG 1.54TR SEER 8.14
498 | Split_Wall_Mounted | York | Y182SH | Non-Inverter | 1.5 | 1.51 | 18238 | 1900 | 9.5989 | 15170 | 2200 | 6.8955 | 8.15 | Split_Wall_Mounted York 1.51TR SEER 8.15 | Split_Wall_Mounted LG 1.54TR SEER 8.14
499 | Split_Wall_Mounted | York | Y242SC / X242SC | Non-Inverter | 2 | 1.74 | 20985 | 2200 | 9.5386 | 18254 | 2600 | 7.0208 | 8.18 | Split_Wall_Mounted York 1.74TR SEER 8.18 | Split_Wall_Mounted LG 1.74TR SEER 8.17
500 | Split_Wall_Mounted | York | X242SH | Non-Inverter | 2 | 1.71 | 20541 | 2160 | 9.5097 | 17743 | 2530 | 7.013 | 8.15 | Split_Wall_Mounted York 1.71TR SEER 8.15 | Split_Wall_Mounted LG 1.54TR SEER 8.14
501 | Split_Wall_Mounted | LG | B2424C / B2424C | Non-Inverter | 2 | 1.82 | 21853 | 1900 | 11.5016 | 18955 | 2290 | 8.2773 | 9.8 | Split_Wall_Mounted LG 1.82TR SEER 9.8 | Split_Wall_Mounted LG 1.82TR SEER 9.79
502 | Split_Wall_Mounted | BOSCH | B2428C / B2428C | Non-Inverter | 2 | 1.77 | 21340 | 1855 | 11.504 | 18443 | 2230 | 8.2704 | 9.79 | Split_Wall_Mounted BOSCH 1.77TR SEER 9.79 | Split_Wall_Mounted LG 1.82TR SEER 9.79
503 | Split_Wall_Mounted | LG | BC18CCL / BC18CCL | Non-Inverter | 1.5 | 1.49 | 17913 | 1480 | 12.1034 | 15354 | 1780 | 8.6258 | 10.27 | Split_Wall_Mounted LG 1.49TR SEER 10.27 | Split_Wall_Mounted Cooline 1.5TR SEER 10.25
504 | Split_Wall_Mounted | York | AR24HCFNBWKX / AR24HCFNBWKN | Non-Inverter | 2 | 1.93 | 23200 | 2340 | 9.9145 | 20230 | 2700 | 7.4926 | 8.56 | Split_Wall_Mounted York 1.93TR SEER 8.56 | Split_Wall_Mounted Carrier 2TR SEER 8.60
505 | Split_Wall_Mounted | BOSCH | AMBC36CCN | Non-Inverter | 3 | 2.71 | 32600 | 2630 | 12.3954 | 28400 | 3150 | 9.0159 | 10.59 | Split_Wall_Mounted BOSCH 2.71TR SEER 10.59 | Split_Wall_Mounted LG 2.5TR SEER 10.43
506 | Split_Wall_Mounted | SAMSUNG | WBAC18LH | Non-Inverter | 1.5 | 1.44 | 17300 | 1400 | 12.3571 | 14700 | 1680 | 8.75 | 10.46 | Split_Wall_Mounted SAMSUNG 1.44TR SEER 10.46 | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
507 | Split_Wall_Mounted | LG | S242MH | Non-Inverter | 2 | 2 | 24000 | 2500 | 9.6 | 20063 | 3035 | 6.6105 | 8.06 | Split_Wall_Mounted LG 2TR SEER 8.06 | Split_Wall_Mounted Zamil 2.12TR SEER 8.09
508 | Split_Wall_Mounted | ACB | LSAC-24H/A | Non-Inverter | 2 | 2 | 24000 | 2500 | 9.6 |  |  |  |  | Split_Wall_Mounted ACB 2TR SEER | Split_Wall_Mounted Zamil 1.99TR SEER9.77
509 | Split_Wall_Mounted | LG | LS-K1822HL | Non-Inverter | 1.5 | 1.5 | 18000 | 1800 | 10 |  |  |  |  | Split_Wall_Mounted LG 1.5TR SEER | Split_Wall_Mounted GREE 1.5TR SEER 9.98
510 | Split_Wall_Mounted | TCL | TAC-18CS/E7 | Non-Inverter | 1.5 | 1.46 | 17530 | 1510 | 11.6093 |  |  |  |  | Split_Wall_Mounted TCL 1.46TR SEER | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
511 | Split_Wall_Mounted | MTC | MTC24CT20N | Non-Inverter | 2 | 1.75 | 21000 | 1750 | 12 |  |  |  |  | Split_Wall_Mounted MTC 1.75TR SEER | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
512 | Split_Wall_Mounted | STARWAY | PTSW24HC | Non-Inverter | 2 | 1.79 | 21500 | 1823 | 11.7937 |  |  |  |  | Split_Wall_Mounted STARWAY 1.79TR SEER | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
513 | Split_Wall_Mounted | TIT | TIS18CH | Non-Inverter | 1.5 | 1.46 | 17530 | 1510 | 11.6093 |  |  |  |  | Split_Wall_Mounted TIT 1.46TR SEER | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
514 | Split_Wall_Mounted | Gree | GWH24ACE-D3NTA1G/I | Non-Inverter | 2 | 1.87 | 22500 | 1836.7347 | 12.25 |  |  |  |  | Split_Wall_Mounted Gree 1.87TR SEER | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
515 | Split_Wall_Mounted | Zamil | ASTW-H36A2/EW-5 | Non-Inverter | 3 | 3 | 36000 | 3600 | 10 |  |  |  |  | Split_Wall_Mounted Zamil 3TR SEER | Split_Wall_Mounted Carrier 2.75TR SEER 8.81
516 | Split_Wall_Mounted | Gree | GWC18QD-D3NTB4D/I | Non-Inverter | 1.5 | 1.5 | 18000 | 1525 | 11.8033 | 14900 | 1773 | 8.4038 | 9.99 | Split_Wall_Mounted Gree 1.5TR SEER 9.99 | Split_Wall_Mounted GREE 1.5TR SEER 9.98
517 | Split_Wall_Mounted | Fuji | FANP24FVSWHE | Non-Inverter | 2 | 1.83 | 22000 | 1850 | 11.8919 |  |  |  |  | Split_Wall_Mounted Fuji 1.83TR SEER | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
518 | Split_Wall_Mounted | Fuji | RSA-24RAT | Non-Inverter | 2 | 1.88 | 22600 | 2520 | 8.9683 |  |  |  |  | Split_Wall_Mounted Fuji 1.88TR SEER | Split_Wall_Mounted Carrier 2TR SEER 8.60
519 | Split_Wall_Mounted | General | GAC-SF2412HT | Non-Inverter | 2 | 1.83 | 22000 | 1850 | 11.8919 |  |  |  |  | Split_Wall_Mounted General 1.83TR SEER | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
520 | Split_Wall_Mounted | Gree | GWH18ACD-D3NTA1G/I | Non-Inverter | 1.5 | 1.5 | 18000 | 1465 | 12.2867 |  |  |  |  | Split_Wall_Mounted Gree 1.5TR SEER | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
521 | Split_Wall_Mounted | Fisher | FSAC-FT18CERA | Non-Inverter | 2 | 1.91 | 23000 | 1917 | 11.9979 |  |  |  |  | Split_Wall_Mounted Fisher 1.91TR SEER | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
522 | Split_Wall_Mounted | Samsung | AQ24FC | Non-Inverter | 1.5 | 1.65 | 19841 | 2040 | 9.726 |  |  |  |  | Split_Wall_Mounted Samsung 1.65TR SEER | Split_Wall_Mounted LG 1.74TR SEER 9.84
523 | Split_Wall_Mounted | Mando | AC-18H-T7 | Non-Inverter | 1.5 | 1.5 | 18000 | 1516 | 11.8734 |  |  |  |  | Split_Wall_Mounted Mando 1.5TR SEER | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
524 | Split_Wall_Mounted | Ravo | RV20T-24H | Non-Inverter | 2 | 1.75 | 21000 | 1721 | 12.2022 |  |  |  |  | Split_Wall_Mounted Ravo 1.75TR SEER | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
525 | Split_Wall_Mounted | Mando | MP-24CDN | Non-Inverter | 2 | 1.78 | 21400 | 1754 | 12.2007 |  |  |  |  | Split_Wall_Mounted Mando 1.78TR SEER | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
526 | Split_Wall_Mounted | Daewoo | DSA-F1883EL-T | Non-Inverter | 1.5 | 1.5 | 18000 | 1485 | 12.1212 |  |  |  |  | Split_Wall_Mounted Daewoo 1.5TR SEER | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
527 | Split_Wall_Mounted | General_Supreme | GST1888C | Non-Inverter | 1.5 | 1.44 | 17300 | 1407 | 12.2957 |  |  |  |  | Split_Wall_Mounted General_Supreme 1.44TR SEER | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
528 | Split_Wall_Mounted | Gree | GWH24AGE-D3NTAIA/I | Non-Inverter | 2 | 1.87 | 22500 | 1837 | 12.2482 |  |  |  |  | Split_Wall_Mounted Gree 1.87TR SEER | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
529 | Split_Wall_Mounted | Gree | GWH18AGD-D3NTA1A/I | Non-Inverter | 1.5 | 1.5 | 18000 | 1464 | 12.2951 |  |  |  |  | Split_Wall_Mounted Gree 1.5TR SEER | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
530 | Split_Wall_Mounted | Gree | GWC18AACD-D3NTA1G/I | Non-Inverter | 1.5 | 1.5 | 18000 | 1482 | 12.1457 |  |  |  |  | Split_Wall_Mounted Gree 1.5TR SEER | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
531 | Split_Wall_Mounted | QUEEN | HQHS120C | Non-Inverter | 1 | 0.99 | 11900 | 978 | 12.1677 |  |  |  |  | Split_Wall_Mounted QUEEN 0.99TR SEER | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
532 | Split_Wall_Mounted | Speed_Cool | SL24HC | Non-Inverter | 2 | 2 | 24000 | 2500 | 9.6 |  |  |  |  | Split_Wall_Mounted Speed_Cool 2TR SEER | Split_Wall_Mounted Zamil 1.99TR SEER9.77
533 | Split_Wall_Mounted | LG | LS-H182TLB1 | Non-Inverter | 1.5 | 1.5 | 18000 | 1900 | 9.4737 |  |  |  |  | Split_Wall_Mounted LG 1.5TR SEER | Split_Wall_Mounted LG 1.46TR SEER 9.8
534 | Split_Wall_Mounted | General | GC-18CT/S23 | Non-Inverter | 1 | 1 | 12000 | 1000 | 12 |  |  |  |  | Split_Wall_Mounted General 1TR SEER | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
535 | Split_Wall_Mounted | Lakes | KT3F-51GW | Non-Inverter | 1.5 | 1.5 | 18000 | 2150 | 8.3721 |  |  |  |  | Split_Wall_Mounted Lakes 1.5TR SEER | Split_Wall_Mounted LG 1.5TR SEER 8.40
536 | Split_Wall_Mounted | Gree | KT3F-45G/J | Non-Inverter | 1.5 | 1.5 | 18000 | 2150 | 8.3721 |  |  |  |  | Split_Wall_Mounted Gree 1.5TR SEER | Split_Wall_Mounted LG 1.5TR SEER 8.40
537 | Split_Wall_Mounted | MTC | MTC30H/7S-T18 | Non-Inverter | 2 | 2.2 | 26500 | 2244 | 11.8093 |  |  |  |  | Split_Wall_Mounted MTC 2.2TR SEER | Split_Wall_Mounted Gree 2.25TR SEER 11.11
538 | Split_Wall_Mounted | Daewoo | DSA-183LH-R | Non-Inverter | 1.5 | 1.5 | 18000 | 2000 | 9 | 15200 | 2300 | 6.6087 | 7.69 | Split_Wall_Mounted Daewoo 1.5TR SEER 7.69 | Split_Wall_Mounted LG 1.5TR SEER 8.40
539 | Split_Wall_Mounted | LG | S182NH ST0 | Non-Inverter | 1.5 | 1.5 | 18017.094 | 2080 | 8.6621 | 15500 | 2370 | 6.5401 | 7.47 | Split_Wall_Mounted LG 1.5TR SEER 7.47 | Split_Wall_Mounted LG 1.46TR SEER 7.56
540 | Split_Wall_Mounted | MTC | MTC24H/7S-T18 | Non-Inverter | 2 | 1.82 | 21850 | 1850 | 11.8108 |  |  |  |  | Split_Wall_Mounted MTC 1.82TR SEER | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
541 | Split_Wall_Mounted | LG | LS-K1827CM | Non-Inverter | 1.5 | 1.5 | 18000 | 2000 | 9 |  |  |  |  | Split_Wall_Mounted LG 1.5TR SEER | Split_Wall_Mounted LG 1.5TR SEER 8.40
542 | Split_Wall_Mounted | Gree | GWH28ACE-D3NTA1G/I | Non-Inverter | 2 | 2.26 | 27200 | 2266 | 12.0035 |  |  |  |  | Split_Wall_Mounted Gree 2.26TR SEER | Split_Wall_Mounted Gree 2.25TR SEER 11.11
543 | Split_Wall_Mounted | Samsung | AQ24UUPNUMG | Non-Inverter | 2 | 2 | 24000 | 2060 | 11.6505 |  |  |  |  | Split_Wall_Mounted Samsung 2TR SEER | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
544 | Split_Wall_Mounted | Samsung | 24CKK01L | Non-Inverter | 2 | 2 | 24000 | 2600 | 9.2308 |  |  |  |  | Split_Wall_Mounted Samsung 2TR SEER | Split_Wall_Mounted Zamil 1.99TR SEER9.77
545 | Split_Wall_Mounted | LUNA | LACX18H-1M | Non-Inverter | 1.5 | 1.48 | 17800 | 1460 | 12.1918 |  |  |  |  | Split_Wall_Mounted LUNA 1.48TR SEER | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
546 | Split_Wall_Mounted | Mando | KT3FR-61GW/S | Non-Inverter | 2 | 1.73 | 20200 | 1750 | 11.5429 | 17700 | 2130 | 8.3099 | 9.84 | Split_Wall_Mounted Mando 1.73TR SEER 9.84 | Split_Wall_Mounted LG 1.74TR SEER 9.84
547 | Split_Wall_Mounted | LG | S242NH ST0 | Non-Inverter | 2 | 1.91 | 22997 | 2630 | 8.7441 | 20063 | 3035 | 6.6105 | 7.55 | Split_Wall_Mounted LG 1.91TR SEER 7.55 | Split_Wall_Mounted LG 1.91TR SEER 7.54
548 | Split_Wall_Mounted | LG | LS-T242CBG | Non-Inverter | 2 | 2 | 24000 | 2525 | 9.505 |  |  |  |  | Split_Wall_Mounted LG 2TR SEER | Split_Wall_Mounted Zamil 1.99TR SEER9.77
549 | Split_Wall_Mounted | Gree | GWC24QE-D3NTB4A/I | Non-Inverter | 2 | 1.83 | 22000 | 1880 | 11.7021 |  |  |  |  | Split_Wall_Mounted Gree 1.83TR SEER | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
550 | Split_Wall_Mounted | CRONY | ASTW-H12A2/ET | Non-Inverter | 1 | 0.94 | 11282.0513 | 1300 | 8.6785 |  |  |  |  | Split_Wall_Mounted CRONY 0.94TR SEER | Split_Wall_Mounted LG 0.95TR SEER 8.3
551 | Split_Wall_Mounted | LG | LS-T182CBG | Non-Inverter | 1.5 | 1.5 | 18000 | 1700 | 10.5882 |  |  |  |  | Split_Wall_Mounted LG 1.5TR SEER | Split_Wall_Mounted Zamil 1.49TR SEER 10.52
552 | Split_Wall_Mounted | LG | LS-H182TNB0 | Non-Inverter | 1.5 | 1.5 | 18000 | 1860 | 9.6774 | 16000 | 2150 | 7.4419 | 8.41 | Split_Wall_Mounted LG 1.5TR SEER 8.41 | Split_Wall_Mounted LG 1.5TR SEER 8.40
553 | Split_Wall_Mounted | General | GC-18CT/S24 | Non-Inverter | 1.5 | 1.5 | 18000 | 1764 | 10.2041 |  |  |  |  | Split_Wall_Mounted General 1.5TR SEER | Split_Wall_Mounted Ugine 1.48TR SEER 10.23
554 | Split_Wall_Mounted | Gree | GWCN18DETD1A4A/I | Non-Inverter | 1.5 | 1.5 | 18000 | 1525 | 11.8033 |  |  |  |  | Split_Wall_Mounted Gree 1.5TR SEER | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
555 | Split_Wall_Mounted | Ugine | UASG12H | Non-Inverter | 1 | 0.96 | 11600 | 970.7 | 11.9501 |  |  |  |  | Split_Wall_Mounted Ugine 0.96TR SEER | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
556 | Split_Wall_Mounted | Midea | MSTE-24HR | Non-Inverter | 2 | 1.79 | 21538.4615 | 2533 | 8.5031 |  |  |  |  | Split_Wall_Mounted Midea 1.79TR SEER | Split_Wall_Mounted Carrier 1.79TR SEER 8.31
557 | Split_Wall_Mounted | General | GC-18-KFC | Non-Inverter | 1.5 | 1.5 | 18000 | 1500 | 12 |  |  |  |  | Split_Wall_Mounted General 1.5TR SEER | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
558 | Split_Wall_Mounted | General | GC-18CT/524 | Non-Inverter | 1.5 | 1.5 | 18000 | 1500 | 12 |  |  |  |  | Split_Wall_Mounted General 1.5TR SEER | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
559 | Split_Wall_Mounted | Unix | GSDAD30H | Non-Inverter | 2 | 1.9 | 22861 | 2787 | 8.2027 |  |  |  |  | Split_Wall_Mounted Unix 1.9TR SEER | Split_Wall_Mounted LG 1.74TR SEER 8.20
560 | Split_Wall_Mounted | York | HTKA18OS-ADR | Non-Inverter | 1.5 | 1.5 | 18000 | 2080 | 8.6538 |  |  |  |  | Split_Wall_Mounted York 1.5TR SEER | Split_Wall_Mounted LG 1.5TR SEER 8.40
561 | Split_Wall_Mounted | LG | S182DH | Non-Inverter | 1.5 | 1.41 | 17026 | 2100 | 8.1076 | 14672 | 2450 | 5.9886 | 6.95 | Split_Wall_Mounted LG 1.41TR SEER 6.95 | Split_Wall_Mounted LG 1.41TR SEER 6.94
562 | Split_Wall_Mounted | Comfort | MSAC-24CHS/GT2 | Non-Inverter | 2 | 1.83 | 22000 | 2767 | 7.9508 |  |  |  |  | Split_Wall_Mounted Comfort 1.83TR SEER | Split_Wall_Mounted Carrier 1.81TR SEER 7.91
563 | Split_Wall_Mounted | Mando | AC-24C-T7 | Non-Inverter | 2 | 1.83 | 22000 | 1867 | 11.7836 |  |  |  |  | Split_Wall_Mounted Mando 1.83TR SEER | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
564 | Split_Wall_Mounted | LG | S322GH | Non-Inverter | 2 | 2.21 | 26529.9145 | 3050 | 8.6983 | 23270 | 3570 | 6.5182 | 7.5 | Split_Wall_Mounted LG 2.21TR SEER 7.5 | Split_Wall_Mounted LG 2.21TR SEER 7.49
565 | Split_Wall_Mounted | Gree | GWC24AGE-D3NTA1Y/I | Non-Inverter | 2 | 1.84 | 22100 | 1865 | 11.8499 |  |  |  |  | Split_Wall_Mounted Gree 1.84TR SEER | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
566 | Split_Wall_Mounted | queen | HQSG1248H6 | Non-Inverter | 2 | 1.87 | 22500 | 1899 | 11.8483 |  |  |  |  | Split_Wall_Mounted queen 1.87TR SEER | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
567 | Split_Wall_Mounted | LG | B2424H | Non-Inverter | 2 | 1.74 | 20950.5519 | 1820 | 11.5113 | 18937 | 2280 | 8.3057 | 9.84 | Split_Wall_Mounted LG 1.74TR SEER 9.84 | Split_Wall_Mounted LG 1.74TR SEER 9.84
568 | Split_Wall_Mounted | LG | Y182SC | Non-Inverter | 1.5 | 1.54 | 18562 | 1950 | 9.519 | 16037 | 2300 | 6.9726 | 8.14 | Split_Wall_Mounted LG 1.54TR SEER 8.14 | Split_Wall_Mounted LG 1.54TR SEER 8.14
569 | Split_Wall_Mounted | Fuji | ROA24UMTAHS | Non-Inverter | 2 | 2.29 | 27500 | 2300 | 11.9565 |  |  |  |  | Split_Wall_Mounted Fuji 2.29TR SEER | Split_Wall_Mounted Gree 2.25TR SEER 11.11
570 | Split_Wall_Mounted | Gree | GWC18ACD-D3NTA1G/I. | Non-Inverter | 2 | 1.87 | 22500 | 1850 | 12.1622 |  |  |  |  | Split_Wall_Mounted Gree 1.87TR SEER | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
571 | Split_Wall_Mounted | LG | LS-K2424HL | Non-Inverter | 2 | 2 | 24000 | 2525 | 9.505 |  |  |  |  | Split_Wall_Mounted LG 2TR SEER | Split_Wall_Mounted Zamil 1.99TR SEER9.77
572 | Split_Wall_Mounted | LG | T2428P | Non-Inverter | 2 | 1.92 | 23042.735 | 2550 | 9.0364 | 20653 | 3000 | 6.8843 | 7.84 | Split_Wall_Mounted LG 1.92TR SEER 7.84 | Split_Wall_Mounted DAEWOO 2TR SEER 7.86
573 | Split_Wall_Mounted | Samsung | AQ24UUPX | Non-Inverter | 2 | 1.83 | 22051.2821 | 2500 | 8.8205 |  |  |  |  | Split_Wall_Mounted Samsung 1.83TR SEER | Split_Wall_Mounted Carrier 2TR SEER 8.60
574 | Split_Wall_Mounted | HomeQueen | HQSG240H | Non-Inverter | 2 | 1.79 | 21500 | 1792 | 11.9978 |  |  |  |  | Split_Wall_Mounted HomeQueen 1.79TR SEER | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
575 | Split_Wall_Mounted | Midea | MOU-18CN1 | Non-Inverter | 1.5 | 1.5 | 18000 | 2020 | 8.9109 |  |  |  |  | Split_Wall_Mounted Midea 1.5TR SEER | Split_Wall_Mounted LG 1.5TR SEER 8.40
576 | Split_Wall_Mounted | Samsung | LH2012033939 | Non-Inverter | 2 | 2 | 24000 | 2424 | 9.901 |  |  |  |  | Split_Wall_Mounted Samsung 2TR SEER | Split_Wall_Mounted Carrier 1.92TR SEER 9.83
577 | Split_Wall_Mounted | Gree | GWH18AGDXFD3NTA1G/I | Non-Inverter | 1.5 | 1.54 | 18500 | 1762 | 10.4994 |  |  |  |  | Split_Wall_Mounted Gree 1.54TR SEER | Split_Wall_Mounted Zamil 1.49TR SEER 10.52
578 | Split_Wall_Mounted | Gree | GWH12AGC-D3NTA1A/I | Non-Inverter | 1 | 0.96 | 11600 | 1450 | 8 |  |  |  |  | Split_Wall_Mounted Gree 0.96TR SEER | Split_Wall_Mounted LG 0.95TR SEER 7.9
579 | Split_Wall_Mounted | General | KSGS183GE | Non-Inverter | 1.5 | 1.5 | 18000 | 2613 | 6.8886 |  |  |  |  | Split_Wall_Mounted General 1.5TR SEER | Split_Wall_Mounted LG 1.41TR SEER 6.94
580 | Split_Wall_Mounted | York | YHGE24XT3CFE | Non-Inverter | 2 | 1.91 | 23000 | 1925 | 11.9481 |  |  |  |  | Split_Wall_Mounted York 1.91TR SEER | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
581 | Split_Wall_Mounted | Falcon | HBPU-3601 | Non-Inverter | 2.5 | 2.5 | 30000 | 2440 | 12.2951 |  |  |  |  | Split_Wall_Mounted Falcon 2.5TR SEER | Split_Wall_Mounted Gree 2.25TR SEER 11.11
582 | Split_Wall_Mounted | LG | X242EC | Non-Inverter | 2 | 1.83 | 22008.3159 | 2200 | 10.0038 | 18254.9597 | 2600 | 7.0211 | 8.43 | Split_Wall_Mounted LG 1.83TR SEER 8.43 | Split_Wall_Mounted Carrier 1.79TR SEER 8.31
583 | Split_Wall_Mounted | LG | LS-T242CB | Non-Inverter | 2 | 2 | 24000 | 2525 | 9.505 |  |  |  |  | Split_Wall_Mounted LG 2TR SEER | Split_Wall_Mounted Zamil 1.99TR SEER9.77
584 | Split_Wall_Mounted | Falcon | FGS24C | Non-Inverter | 2 | 1.83 | 22000 | 2315 | 9.5032 |  |  |  |  | Split_Wall_Mounted Falcon 1.83TR SEER | Split_Wall_Mounted Zamil 1.99TR SEER9.77
585 | Split_Wall_Mounted | LG | LS-C322MMB0 | Non-Inverter | 2.5 | 2.66 | 32000 | 3350 | 9.5522 |  |  |  |  | Split_Wall_Mounted LG 2.66TR SEER | Split_Wall_Mounted LG 2.58TR SEER 9.72
586 | Split_Wall_Mounted | LG | LS-K1822CL | Non-Inverter | 1.5 | 1.5 | 18000 | 1900 | 9.4737 |  |  |  |  | Split_Wall_Mounted LG 1.5TR SEER | Split_Wall_Mounted LG 1.46TR SEER 9.8
587 | Split_Wall_Mounted | Rowa | CS-RW18H | Non-Inverter | 1.5 | 1.46 | 17530 | 1510 | 11.6093 |  |  |  |  | Split_Wall_Mounted Rowa 1.46TR SEER | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
588 | Split_Wall_Mounted | ACB | LSAC-24H | Non-Inverter | 2 | 2 | 24000 | 2500 | 9.6 |  |  |  |  | Split_Wall_Mounted ACB 2TR SEER | Split_Wall_Mounted Zamil 1.99TR SEER9.77
589 | Split_Wall_Mounted | Gibson | SXSA24CE73Y1 | Non-Inverter | 2 | 2.25 | 27000 | 2213 | 12.2006 |  |  |  |  | Split_Wall_Mounted Gibson 2.25TR SEER | Split_Wall_Mounted Gree 2.25TR SEER 11.11
590 | Split_Wall_Mounted | Carrier | 42EGQ024-3 | Non-Inverter | 2 | 1.75 | 21000 | 2330 | 9.0129 |  |  |  |  | Split_Wall_Mounted Carrier 1.75TR SEER | Split_Wall_Mounted Carrier 1.79TR SEER 8.31
591 | Split_Wall_Mounted | Carrier | 42QBL025-3 | Non-Inverter | 2 | 2 | 24000 | 2770 | 8.6643 |  |  |  |  | Split_Wall_Mounted Carrier 2TR SEER | Split_Wall_Mounted Carrier 2TR SEER 8.60
592 | Split_Wall_Mounted | Trane | MCW524S100RA | Non-Inverter | 2 | 1.83 | 22000 | 2600 | 8.4615 |  |  |  |  | Split_Wall_Mounted Trane 1.83TR SEER | Split_Wall_Mounted Carrier 2TR SEER 8.60
593 | Split_Wall_Mounted | KOOLEN | KOACS18KHC | Non-Inverter | 1.5 | 1.49 | 17900 | 1486 | 12.0458 |  |  |  |  | Split_Wall_Mounted KOOLEN 1.49TR SEER | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
594 | Split_Wall_Mounted | LG | LS-K2422HL | Non-Inverter | 2 | 2 | 24000 | 2525 | 9.505 |  |  |  |  | Split_Wall_Mounted LG 2TR SEER | Split_Wall_Mounted Zamil 1.99TR SEER9.77
595 | Split_Wall_Mounted | Gaint | GNT12CCG | Non-Inverter | 1 | 0.88 | 10577 | 900 | 11.7522 |  |  |  |  | Split_Wall_Mounted Gaint 0.88TR SEER | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
596 | Split_Wall_Mounted | LG | LS-M3221AL | Non-Inverter | 2.5 | 2.66 | 32000 | 3350 | 9.5522 |  |  |  |  | Split_Wall_Mounted LG 2.66TR SEER | Split_Wall_Mounted LG 2.58TR SEER 9.72
597 | Split_Wall_Mounted | Caus | CAUS-24HRF1 | Non-Inverter | 2 | 2 | 24000 | 3000 | 8 |  |  |  |  | Split_Wall_Mounted Caus 2TR SEER | Split_Wall_Mounted Carrier 1.81TR SEER 7.91
598 | Split_Wall_Mounted | LG | LS-H322MMBO | Non-Inverter | 2.5 | 2.66 | 32000 | 3200 | 10 |  |  |  |  | Split_Wall_Mounted LG 2.66TR SEER | Split_Wall_Mounted Zamil 2.62TR SEER 10.00
599 | Split_Wall_Mounted | Mando | F19M-24HT | Non-Inverter | 2 | 1.8 | 21600 | 1742 | 12.3995 |  |  |  |  | Split_Wall_Mounted Mando 1.8TR SEER | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
600 | Split_Wall_Mounted | LG | LS-T244CBG | Non-Inverter | 2 | 2 | 24000 | 2525 | 9.505 |  |  |  |  | Split_Wall_Mounted LG 2TR SEER | Split_Wall_Mounted Zamil 1.99TR SEER9.77
601 | Split_Wall_Mounted | Kelvinator | KTS18H | Non-Inverter | 1.5 | 1.5 | 18000 | 1500 | 12 |  |  |  |  | Split_Wall_Mounted Kelvinator 1.5TR SEER | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
602 | Split_Wall_Mounted | Classic | ADO18CHXOW | Non-Inverter | 1.5 | 1.47 | 17700 | 1532 | 11.5535 | 14798 | 1783 | 8.2995 | 9.81 | Split_Wall_Mounted Classic 1.47TR SEER 9.81 | Split_Wall_Mounted LG 1.46TR SEER 9.8
603 | Split_Wall_Mounted | LG | S242KH | Non-Inverter | 2 | 2 | 24000 | 2450 | 9.7959 | 19278 | 2850 | 6.7642 | 8.2 | Split_Wall_Mounted LG 2TR SEER 8.2 | Split_Wall_Mounted Zamil 1.95TR SEER 8.11
604 | Split_Wall_Mounted | Samsung | 24000BTU | Non-Inverter | 2 | 2 | 24000 | 2424 | 9.901 |  |  |  |  | Split_Wall_Mounted Samsung 2TR SEER | Split_Wall_Mounted Carrier 1.92TR SEER 9.83
605 | Split_Wall_Mounted | Carrier | 42QKA0243P | Non-Inverter | 2 | 1.79 | 21500 | 1762 | 12.202 |  |  |  |  | Split_Wall_Mounted Carrier 1.79TR SEER | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
606 | Split_Wall_Mounted | Mando | AC-30H-T7 | Non-Inverter | 2 | 2.2 | 26500 | 2244 | 11.8093 |  |  |  |  | Split_Wall_Mounted Mando 2.2TR SEER | Split_Wall_Mounted Gree 2.25TR SEER 11.11
607 | Split_Wall_Mounted | Ravo | RV-20T-24 | Non-Inverter | 2 | 1.75 | 21059.8291 | 1721 | 12.237 |  |  |  |  | Split_Wall_Mounted Ravo 1.75TR SEER | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
608 | Split_Wall_Mounted | koolen | Koacs12khc | Non-Inverter | 1 | 0.96 | 11600 | 1143 | 10.1487 |  |  |  |  | Split_Wall_Mounted koolen 0.96TR SEER | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
609 | Split_Wall_Mounted | Carrier | 42QHDO-24 | Non-Inverter | 2 | 1.75 | 21000 | 2386 | 8.8013 |  |  |  |  | Split_Wall_Mounted Carrier 1.75TR SEER | Split_Wall_Mounted Carrier 1.79TR SEER 8.31
610 | Split_Wall_Mounted | Super_General | KSG243GE | Non-Inverter | 2 | 1.75 | 21000 | 1750 | 12 |  |  |  |  | Split_Wall_Mounted Super_General 1.75TR SEER | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
611 | Split_Wall_Mounted | Midea | MSTE-18HR-E1 | Non-Inverter | 1.5 | 1.39 | 16752.1368 | 2042 | 8.2038 |  |  |  |  | Split_Wall_Mounted Midea 1.39TR SEER | Split_Wall_Mounted LG 1.52TR SEER 8.15
612 | Split_Wall_Mounted | Fisher | FSAC-FT36CERA | Non-Inverter | 2.5 | 2.6 | 31200 | 2537 | 12.298 |  |  |  |  | Split_Wall_Mounted Fisher 2.6TR SEER | Split_Wall_Mounted LG 2.5TR SEER 10.43
613 | Split_Wall_Mounted | Falcon | FMS12H9 | Non-Inverter | 1 | 0.98 | 11800 | 952 | 12.395 |  |  |  |  | Split_Wall_Mounted Falcon 0.98TR SEER | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
614 | Split_Wall_Mounted | TERIM | TRG24CS19N | Non-Inverter | 2 | 1.83 | 22000 | 1864 | 11.8026 |  |  |  |  | Split_Wall_Mounted TERIM 1.83TR SEER | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
615 | Split_Wall_Mounted | YOKO | YOKO-24CH | Non-Inverter | 2 | 1.84 | 22178 | 1912 | 11.5994 |  |  |  |  | Split_Wall_Mounted YOKO 1.84TR SEER | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
616 | Split_Wall_Mounted | Super_General | KSG311GER | Non-Inverter | 2 | 2.2 | 26400 | 2129 | 12.4002 |  |  |  |  | Split_Wall_Mounted Super_General 2.2TR SEER | Split_Wall_Mounted Gree 2.25TR SEER 11.11
617 | Split_Wall_Mounted | Mando | AC-24H-T7 | Non-Inverter | 2 | 1.83 | 22050 | 1856.3731 | 11.878 |  |  |  |  | Split_Wall_Mounted Mando 1.83TR SEER | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
618 | Split_Wall_Mounted | Fuji | RSA30LMTA-9 | Non-Inverter | 2 | 2.29 | 27500 | 2300 | 11.9565 |  |  |  |  | Split_Wall_Mounted Fuji 2.29TR SEER | Split_Wall_Mounted Gree 2.25TR SEER 11.11
619 | Split_Wall_Mounted | Falcon | ACSU24N | Non-Inverter | 2 | 2 | 24000 | 2770 | 8.6643 |  |  |  |  | Split_Wall_Mounted Falcon 2TR SEER | Split_Wall_Mounted Carrier 2TR SEER 8.60
620 | Split_Wall_Mounted | Craft | DSSA32EE7 | Non-Inverter | 2.5 | 2.5 | 30000 | 3450 | 8.6957 |  |  |  |  | Split_Wall_Mounted Craft 2.5TR SEER | Split_Wall_Mounted Fuji 2.2TR SEER 8.66
621 | Split_Wall_Mounted | LG | S122DH | Non-Inverter | 1 | 1 | 12000 | 1150 | 10.4348 | 9383 | 1300 | 7.2177 | 8.73 | Split_Wall_Mounted LG 1TR SEER 8.73 | Split_Wall_Mounted LG 0.95TR SEER 8.3
622 | Split_Wall_Mounted | LG | LS-R122AAG | Non-Inverter | 1 | 1 | 12000 | 1220 | 9.8361 |  |  |  |  | Split_Wall_Mounted LG 1TR SEER | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
623 | Split_Wall_Mounted | Haam | HM24C5M20 | Non-Inverter | 2 | 1.83 | 22000 | 1781.37 | 12.35 |  |  |  |  | Split_Wall_Mounted Haam 1.83TR SEER | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
624 | Split_Wall_Mounted | Mando | F19M-12CT | Non-Inverter | 1 | 1.05 | 12600 | 1024 | 12.3047 |  |  |  |  | Split_Wall_Mounted Mando 1.05TR SEER | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
625 | Split_Wall_Mounted | Ugine | UGN12 | Non-Inverter | 1 | 0.93 | 11260 | 1237 | 9.1027 |  |  |  |  | Split_Wall_Mounted Ugine 0.93TR SEER | Split_Wall_Mounted LG 0.95TR SEER 8.3
626 | Split_Wall_Mounted | Mando | F19M-30CT | Non-Inverter | 2 | 2.23 | 26800 | 2161 | 12.4017 |  |  |  |  | Split_Wall_Mounted Mando 2.23TR SEER | Split_Wall_Mounted Gree 2.25TR SEER 11.11
627 | Split_Wall_Mounted | Craft | DSXSA32FE7 | Non-Inverter | 2.5 | 2.5 | 30000 | 3450 | 8.6957 |  |  |  |  | Split_Wall_Mounted Craft 2.5TR SEER | Split_Wall_Mounted Fuji 2.2TR SEER 8.66
628 | Split_Wall_Mounted | LG | LS-M3221BL | Non-Inverter | 2.5 | 2.66 | 32000 | 3350 | 9.5522 |  |  |  |  | Split_Wall_Mounted LG 2.66TR SEER | Split_Wall_Mounted LG 2.58TR SEER 9.72
629 | Split_Wall_Mounted | LG | S242SHU51 | Non-Inverter | 2 | 1.87 | 22520.1372 | 2640 | 8.5304 | 18947.5 | 3250 | 5.83 | 7.15 | Split_Wall_Mounted LG 1.87TR SEER 7.15 | Split_Wall_Mounted LG 1.87TR SEER 7.14
630 | Split_Wall_Mounted | Mando | F23TP-18CT | Non-Inverter | 1.5 | 1.53 | 18400 | 1484 | 12.3989 | 15300 | 1800 | 8.5 | 10.39 | Split_Wall_Mounted Mando 1.53TR SEER 10.39 | Split_Wall_Mounted Mando 1.53TR SEER 10.38
631 | Split_Wall_Mounted | York | YTHA18OSAADA | Non-Inverter | 1.5 | 1.5 | 18000 | 2094 | 8.596 |  |  |  |  | Split_Wall_Mounted York 1.5TR SEER | Split_Wall_Mounted LG 1.5TR SEER 8.40
632 | Split_Wall_Mounted | Queen | HQ8G1240H6 | Non-Inverter | 2 | 1.87 | 22500 | 1875 | 12 |  |  |  |  | Split_Wall_Mounted Queen 1.87TR SEER | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
633 | Split_Wall_Mounted | GoldStar | Model.11GoldStar | Non-Inverter | 2 | 2 | 24000 | 2500 | 9.6 | 19600 | 3000 | 6.5333 | 8.02 | Split_Wall_Mounted GoldStar 2TR SEER 8.02 | Split_Wall_Mounted Zamil 2.12TR SEER 8.09
634 | Split_Wall_Mounted | LG | S322GHSD0 | Non-Inverter | 2.5 | 2.66 | 32000 | 3000 | 10.6667 |  |  |  |  | Split_Wall_Mounted LG 2.66TR SEER | Split_Wall_Mounted LG 2.5TR SEER 10.43
635 | Split_Wall_Mounted | Petra | Petra NA | Non-Inverter | 2 | 1.79 | 21538.4615 | 2700 | 7.9772 |  |  |  |  | Split_Wall_Mounted Petra 1.79TR SEER | Split_Wall_Mounted Carrier 1.81TR SEER 7.91
636 | Split_Wall_Mounted | O2 | O2- NA 1.83 | Non-Inverter | 2 | 1.83 | 22000 | 1781 | 12.3526 |  |  |  |  | Split_Wall_Mounted O2 1.83TR SEER | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
637 | Split_Wall_Mounted | Carrier | 38QKA0243 | Non-Inverter | 2 | 1.79 | 21500 | 1762 | 12.202 | 18500 | 2126 | 8.7018 | 10.36 | Split_Wall_Mounted Carrier 1.79TR SEER 10.36 | Split_Wall_Mounted Carrier 1.79TR SEER 10.35
638 | Split_Wall_Mounted | Zamil | ADO36CHXCW | Non-Inverter | 2.5 | 2.62 | 31499.5735 | 2669 | 11.802 | 27998.8627 | 3373 | 8.3009 | 10.01 | Split_Wall_Mounted Zamil 2.62TR SEER 10.01 | Split_Wall_Mounted Zamil 2.62TR SEER 10.00
639 | Split_Wall_Mounted | York | S1ZI18300 | Non-Inverter | 1.5 | 1.5 | 18000 | 2000 | 9 |  |  |  |  | Split_Wall_Mounted York 1.5TR SEER | Split_Wall_Mounted LG 1.5TR SEER 8.40
640 | Split_Wall_Mounted | York | NYVR243M-0S3 | Non-Inverter | 2 | 1.83 | 22000 | 2530 | 8.6957 | 18470 | 2980 | 6.198 | 7.37 | Split_Wall_Mounted York 1.83TR SEER 7.37 | Split_Wall_Mounted LG 1.79TR SEER 7.34
641 | Split_Wall_Mounted | York | ANJ18BDC1T | Non-Inverter | 1.5 | 1.5 | 18028 | 1857 | 9.7081 | 14465 | 2077 | 6.9644 | 8.21 | Split_Wall_Mounted York 1.5TR SEER 8.21 | Split_Wall_Mounted LG 1.52TR SEER 8.15
642 | Split_Wall_Mounted | York | S1ZDA18300 / S1ZI18300 | Non-Inverter | 1.5 | 1.5 | 18000 | 2000 | 9 |  |  |  |  | Split_Wall_Mounted York 1.5TR SEER | Split_Wall_Mounted LG 1.5TR SEER 8.40
643 | Split_Wall_Mounted | LG | B1ZA18300 / B1ZDI18300 | Non-Inverter | 1.5 | 1.5 | 18000 | 2000 | 9 |  |  |  |  | Split_Wall_Mounted LG 1.5TR SEER | Split_Wall_Mounted LG 1.5TR SEER 8.40
644 | Split_Wall_Mounted | LG | S1ZDA24300 / S1ZDI24300 | Non-Inverter | 2 | 2 | 24000 | 2360 | 10.1695 |  |  |  |  | Split_Wall_Mounted LG 2TR SEER | Split_Wall_Mounted Gree 1.83TR SEER 10.17
645 | Split_Wall_Mounted | LG | E182EC | Non-Inverter | 1.5 | 1.64 | 19738 | 2035 | 9.6993 | 17488 | 2500 | 6.9952 | 8.28 | Split_Wall_Mounted LG 1.64TR SEER 8.28 | Split_Wall_Mounted LG 1.53TR SEER 8.30
646 | Split_Wall_Mounted | York | Z182EC SN4 | Non-Inverter | 1.5 | 1.5 | 18000 | 2110 | 8.5308 | 15320 | 2500 | 6.128 | 7.25 | Split_Wall_Mounted York 1.5TR SEER 7.25 | Split_Wall_Mounted LG 1.46TR SEER 7.28
647 | Split_Wall_Mounted | LG | LV-H24BLA3 | Non-Inverter | 2 | 2 | 24064 | 2200 | 10.9382 | 21000 | 2600 | 8.0769 | 9.38 | Split_Wall_Mounted LG 2TR SEER 9.38 | Split_Wall_Mounted Zamil 1.99TR SEER9.77
648 | Split_Wall_Mounted | Classic | KXC24CSICIQ - ADX24ECAXFQ | Non-Inverter | 2 | 1.99 | 23993 | 3000 | 7.9977 | 19493 | 3290 | 5.9249 | 6.83 | Split_Wall_Mounted Classic 1.99TR SEER 6.83 | Split_Wall_Mounted Zamil 2TR SEER 6.69
649 | Split_Wall_Mounted | Classic | KXC24CSSHIV - ADU24CHAXFV | Non-Inverter | 2 | 1.95 | 23498 | 2460 | 9.552 | 20100 | 2935 | 6.8484 | 8.12 | Split_Wall_Mounted Classic 1.95TR SEER 8.12 | Split_Wall_Mounted Zamil 1.95TR SEER 8.11
650 | Split_Wall_Mounted | Classic | KRC24CDMCJOW2 - ADO24CCXOW2 | Non-Inverter | 2 | 1.92 | 23048 | 1937 | 11.8988 | 18698 | 2174 | 8.6007 | 10.09 | Split_Wall_Mounted Classic 1.92TR SEER 10.09 | Split_Wall_Mounted Carrier 1.83TR SEER 10.08
651 | Split_Wall_Mounted | Classic | KRC24CDSHJED1 - ADM24CHXED1 | Non-Inverter | 2 | 1.88 | 22600 | 1823 | 12.3971 | 19500 | 2321 | 8.4016 | 10.38 | Split_Wall_Mounted Classic 1.88TR SEER 10.38 | Split_Wall_Mounted Giant 1.75TR SEER 10.36
652 | Split_Wall_Mounted | Classic | KRC24CDMCJOW1 - ADO24CCXOW1 | Non-Inverter | 2 | 2.03 | 24396 | 2113 | 11.5457 | 19599 | 2361 | 8.3011 | 9.77 | Split_Wall_Mounted Classic 2.03TR SEER 9.77 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
653 | Split_Wall_Mounted | Gree | GWC24ACE-D3NTA1A/O | Non-Inverter | 2 | 1.83 | 22000 | 1880 | 11.7021 | 18300 | 2200 | 8.3182 | 9.9 | Split_Wall_Mounted Gree 1.83TR SEER 9.9 | Split_Wall_Mounted LG 1.74TR SEER 9.84
654 | Split_Wall_Mounted | Gree | GWC24QE-D3NTA1F/O | Non-Inverter | 2 | 1.83 | 22000 | 1880 | 11.7021 | 18700 | 2255 | 8.2927 | 9.91 | Split_Wall_Mounted Gree 1.83TR SEER 9.91 | Split_Wall_Mounted LG 1.74TR SEER 9.84
655 | Split_Wall_Mounted | Haier | HSU-24LZE13/R2 | Non-Inverter | 2 | 1.83 | 22000 | 1850 | 11.8919 | 19500 | 2250 | 8.6667 | 10.18 | Split_Wall_Mounted Haier 1.83TR SEER 10.18 | Split_Wall_Mounted Gree 1.83TR SEER 10.17
656 | Split_Wall_Mounted | LG | NT242C | Non-Inverter | 2 | 1.83 | 22000 | 1833 | 12.0022 | 18500 | 2126 | 8.7018 | 10.22 | Split_Wall_Mounted LG 1.83TR SEER 10.22 | Split_Wall_Mounted Gree 1.83TR SEER 10.17
657 | Split_Wall_Mounted | LG | A242SC NC0 | Non-Inverter | 2 | 1.76 | 21189 | 1840 | 11.5158 | 17981 | 2170 | 8.2862 | 9.79 | Split_Wall_Mounted LG 1.76TR SEER 9.79 | Split_Wall_Mounted LG 1.82TR SEER 9.79
658 | Split_Wall_Mounted | LG | NC242C3 | Inverter | 2 | 2 | 24000 | 1832 | 13.1004 | 22000 | 2417 | 9.1022 | 11.1 | Split_Wall_Mounted LG 2TR SEER 11.1 | Inverter unit "No replacement"
659 | Split_Wall_Mounted | Zamil | MRZ24CDGHIAW | Non-Inverter | 2 | 1.9 | 22898 | 1982 | 11.553 | 19599 | 2360 | 8.3047 | 9.83 | Split_Wall_Mounted Zamil 1.9TR SEER 9.83 | Split_Wall_Mounted Carrier 1.92TR SEER 9.83
660 | Split_Wall_Mounted | Zamil | KZC24CSPCIQ | Non-Inverter | 2 | 1.85 | 22297 | 2850 | 7.8235 | 19697 | 3300 | 5.9688 | 6.78 | Split_Wall_Mounted Zamil 1.85TR SEER 6.78 | Split_Wall_Mounted Zamil 2TR SEER 6.69
661 | Split_Wall_Mounted | LG | S182DHN51 | Non-Inverter | 1.5 | 1.41 | 17025 | 2100 | 8.1071 | 14672 | 2450 | 5.9886 | 6.95 | Split_Wall_Mounted LG 1.41TR SEER 6.95 | Split_Wall_Mounted LG 1.41TR SEER 6.94
662 | Split_Wall_Mounted | Ugine | UTS18LSHRN-7 | Non-Inverter | 1.5 | 1.5 | 18000 | 1525 | 11.8033 | 14900 | 1773 | 8.4038 | 9.99 | Split_Wall_Mounted Ugine 1.5TR SEER 9.99 | Split_Wall_Mounted GREE 1.5TR SEER 9.98
663 | Split_Wall_Mounted | York | YK9FXC018BAH-AX | Non-Inverter | 1.5 | 1.5 | 18000 | 1500 | 12 | 16000 | 1720 | 9.3023 | 10.44 | Split_Wall_Mounted York 1.5TR SEER 10.44 | Split_Wall_Mounted LG 1.5TR SEER 10.46
664 | Split_Wall_Mounted | York | YHGE18YT3CFEO-3 | Non-Inverter | 1.5 | 1.5 | 18000 | 1475 | 12.2034 | 15000 | 1725 | 8.6957 | 10.33 | Split_Wall_Mounted York 1.5TR SEER 10.33 | Split_Wall_Mounted Mando 1.5TR SEER 10.35
665 | Split_Wall_Mounted | Zamil | KRZ18CDACIAD | Non-Inverter | 1.5 | 1.5 | 18015 | 1374 | 13.1114 | 15000 | 1765 | 8.4986 | 10.81 | Split_Wall_Mounted Zamil 1.5TR SEER 10.81 | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
666 | Split_Wall_Mounted | Mando | AC-18C-MDE | Non-Inverter | 1.5 | 1.53 | 18400 | 1560 | 11.7949 | 16600 | 1860 | 8.9247 | 10.21 | Split_Wall_Mounted Mando 1.53TR SEER 10.21 | Split_Wall_Mounted Ugine 1.48TR SEER 10.23
667 | Split_Wall_Mounted | Classic | KRC30CDSHJCW2 - ADO30CHXCW2 | Non-Inverter | 2 | 2.29 | 27497 | 2320 | 11.8522 | 24198 | 2847 | 8.4995 | 10.1 | Split_Wall_Mounted Classic 2.29TR SEER 10.1 | Split_Wall_Mounted GREE 2.19TR SEER 10.05
668 | Split_Wall_Mounted | LG | S122NCNE2 | Non-Inverter | 1 | 1 | 12010 | 1200 | 10.0083 | 10577 | 1400 | 7.555 | 8.64 | Split_Wall_Mounted LG 1TR SEER 8.64 | Split_Wall_Mounted LG 0.95TR SEER 8.3
669 | Split_Wall_Mounted | LG | S322GCND4 | Non-Inverter | 2 | 2.24 | 26989 | 3210 | 8.4078 | 23748 | 3690 | 6.4358 | 7.29 | Split_Wall_Mounted LG 2.24TR SEER 7.29 | Split_Wall_Mounted LG 2.25TR SEER 7.28
670 | Split_Wall_Mounted | LG | A3024CUV0 | Non-Inverter | 2 | 1.99 | 23986 | 2080 | 11.5317 | 20779 | 2510 | 8.2785 | 9.81 | Split_Wall_Mounted LG 1.99TR SEER 9.81 | Split_Wall_Mounted LG 1.99TR SEER 9.80
671 | Split_Wall_Mounted | LG | T3624CNV0 | Non-Inverter | 2.5 | 2.58 | 31015 | 2710 | 11.4446 | 24805 | 2960 | 8.3801 | 9.73 | Split_Wall_Mounted LG 2.58TR SEER 9.73 | Split_Wall_Mounted LG 2.58TR SEER 9.72
672 | Split_Wall_Mounted | Zamil | KRZ30CDGHIFW | Non-Inverter | 2 | 2.18 | 26197 | 2239 | 11.7003 | 23000 | 2771 | 8.3003 | 9.93 | Split_Wall_Mounted Zamil 2.18TR SEER 9.93 | Split_Wall_Mounted Zamil 2.35TR SEER 9.85
673 | Split_Wall_Mounted | Carrier | 42KHA024HSN | Non-Inverter | 2 | 1.83 | 22000 | 1781 | 12.3526 | 18200 | 2128 | 8.5526 | 10.37 | Split_Wall_Mounted Carrier 1.83TR SEER 10.37 | Split_Wall_Mounted Giant 1.75TR SEER 10.36
674 | Split_Wall_Mounted | Carrier | 42EQG024-3 | Non-Inverter | 2 | 1.75 | 21000 | 2330 | 9.0129 |  |  |  |  | Split_Wall_Mounted Carrier 1.75TR SEER | Split_Wall_Mounted Carrier 1.79TR SEER 8.31
675 | Split_Wall_Mounted | Carrier | 42EGQ018-3 | Non-Inverter | 1.5 | 1.5 | 18000 | 1895 | 9.4987 |  |  |  |  | Split_Wall_Mounted Carrier 1.5TR SEER | Split_Wall_Mounted LG 1.46TR SEER 9.8
676 | Split_Wall_Mounted | Carrier | 42KHC018-3B | Non-Inverter | 1.5 | 1.5 | 18000 | 2022 | 8.9021 | 16200 | 2382 | 6.801 | 7.73 | Split_Wall_Mounted Carrier 1.5TR SEER 7.73 | Split_Wall_Mounted Royal Temp 1.5TR SEER 7.67
677 | Split_Wall_Mounted | Carrier | 42CKA0183P | Non-Inverter | 1.5 | 1.5 | 18000 | 1475 | 12.2034 | 15800 | 1756 | 8.9977 | 10.47 | Split_Wall_Mounted Carrier 1.5TR SEER 10.47 | Split_Wall_Mounted LG 1.5TR SEER 10.46
678 | Split_Wall_Mounted | Carrier | 42KHA018HSN-1 | Non-Inverter | 1.5 | 1.5 | 18000 | 1513 | 11.8969 | 15500 | 1802 | 8.6016 | 10.14 | Split_Wall_Mounted Carrier 1.5TR SEER 10.14 | Split_Wall_Mounted LG 1.47TR SEER 10.15
679 | Split_Wall_Mounted | Carrier | 42KHB018HS | Non-Inverter | 1.5 | 1.54 | 18500 | 1530 | 12.0915 | 16500 | 1800 | 9.1667 | 10.47 | Split_Wall_Mounted Carrier 1.54TR SEER 10.47 | Split_Wall_Mounted LG 1.5TR SEER 10.46
680 | Split_Wall_Mounted | Carrier | 42KHB024HS | Non-Inverter | 2 | 2 | 24000 | 1960 | 12.2449 | 21000 | 2350 | 8.9362 | 10.47 | Split_Wall_Mounted Carrier 2TR SEER 10.47 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
681 | Split_Wall_Mounted | Carrier | 42XPLO30H3P | Non-Inverter | 2 | 2.25 | 27000 | 2260 | 11.9469 | 24000 | 2700 | 8.8889 | 10.29 | Split_Wall_Mounted Carrier 2.25TR SEER 10.29 | Split_Wall_Mounted Gree 2.25TR SEER 11.11
682 | Split_Wall_Mounted | General | ASSA18FMTA | Non-Inverter | 1.5 | 1.55 | 18600 | 1610 | 11.5528 | 15900 | 1920 | 8.2812 | 9.82 | Split_Wall_Mounted General 1.55TR SEER 9.82 | Split_Wall_Mounted LG 1.46TR SEER 9.8
683 | Split_Wall_Mounted | Carrier | 42KFH024-0S6 | Non-Inverter | 2 | 1.83 | 22000 | 1811 | 12.148 | 19000 | 2222 | 8.5509 | 10.28 | Split_Wall_Mounted Carrier 1.83TR SEER 10.28 | Split_Wall_Mounted LG 1.83TR SEER 10.27
684 | Split_Wall_Mounted | York | HTEA24OS-ADR | Non-Inverter | 2 | 2 | 24000 | 2650 | 9.0566 |  |  |  |  | Split_Wall_Mounted York 2TR SEER | Split_Wall_Mounted Carrier 2TR SEER 8.60
685 | Split_Wall_Mounted | White Westinghouse | WWS18KDHI | Non-Inverter | 1.5 | 1.5 | 18000 | 1485 | 12.1212 | 15600 | 1785 | 8.7395 | 10.33 | Split_Wall_Mounted White Westinghouse 1.5TR SEER 10.33 | Split_Wall_Mounted Mando 1.5TR SEER 10.35
686 | Split_Wall_Mounted | LG | S242DP S51 | Non-Inverter | 2 | 2 | 24000 | 2350 | 10.2128 | 19650 | 2840 | 6.919 | 8.52 | Split_Wall_Mounted LG 2TR SEER 8.52 | Split_Wall_Mounted Carrier 2TR SEER 8.60
687 | Split_Wall_Mounted | General | ASSA24FMTA | Non-Inverter | 2 | 1.88 | 22600 | 1960 | 11.5306 | 19500 | 2350 | 8.2979 | 9.82 | Split_Wall_Mounted General 1.88TR SEER 9.82 | Split_Wall_Mounted LG 1.99TR SEER 9.80
688 | Split_Wall_Mounted | Carrier | 38XPL036H3 | Non-Inverter | 2.5 | 2.62 | 31500 | 2640 | 11.9318 | 28000 | 3190 | 8.7774 | 10.24 | Split_Wall_Mounted Carrier 2.62TR SEER 10.24 | Split_Wall_Mounted Carrier 2.58TR SEER 10.41
689 | Split_Wall_Mounted | LG | S242KC st2 | Non-Inverter | 2 | 2 | 24000 | 2350 | 10.2128 | 19722 | 2700 | 7.3044 | 8.65 | Split_Wall_Mounted LG 2TR SEER 8.65 | Split_Wall_Mounted Carrier 2TR SEER 8.60
690 | Split_Wall_Mounted | LG | LS-K2422CL | Non-Inverter | 2 | 2 | 24000 | 2100 | 11.4286 |  |  |  |  | Split_Wall_Mounted LG 2TR SEER | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
691 | Split_Wall_Mounted | PlasmaGold | LS-C242TGM0 | Non-Inverter | 2 | 2 | 24000 | 2350 | 10.2128 | 19722.18 | 2700 | 7.3045 | 8.65 | Split_Wall_Mounted PlasmaGold 2TR SEER 8.65 | Split_Wall_Mounted Carrier 2TR SEER 8.60
692 | Split_Wall_Mounted | LG | T2421C nc0 | Non-Inverter | 2 | 2 | 24000 | 2500 | 9.6 | 19312 | 2840 | 6.8 | 8.1 | Split_Wall_Mounted LG 2TR SEER 8.1 | Split_Wall_Mounted Zamil 2.12TR SEER 8.09
693 | Split_Wall_Mounted | Midea | MSTEP24CRNF6 | Non-Inverter | 2 | 1.75 | 21000 | 1770 | 11.8644 | 18200 | 2130 | 8.5446 | 10.11 | Split_Wall_Mounted Midea 1.75TR SEER 10.11 | Split_Wall_Mounted Carrier 1.83TR SEER 10.08
694 | Split_Wall_Mounted | York | YHFE24XT3CFE-R4 | Non-Inverter | 2 | 1.83 | 22000 | 1775 | 12.3944 | 19000 | 2200 | 8.6364 | 10.46 | Split_Wall_Mounted York 1.83TR SEER 10.46 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
695 | Split_Wall_Mounted | LG | B2424H N51 | Inverter | 2 | 1.75 | 21951 | 1820 | 12.061 | 18937 | 2280 | 8.3057 | 10.14 | Split_Wall_Mounted LG 1.75TR SEER 10.14 | Inverter unit "No replacement"
696 | Split_Wall_Mounted | LG | S242NC N52 | Non-Inverter | 2 | 1.83 | 22000 | 2500 | 8.8 | 19100 | 3000 | 6.3667 | 7.51 | Split_Wall_Mounted LG 1.83TR SEER 7.51 | Split_Wall_Mounted Zamil 1.83TR SEER 7.51
697 | Split_Wall_Mounted | LG | GG24KCN | Non-Inverter | 2 | 1.75 | 21000 | 1770 | 11.8644 | 18200 | 2130 | 8.5446 | 10.11 | Split_Wall_Mounted LG 1.75TR SEER 10.11 | Split_Wall_Mounted Carrier 1.83TR SEER 10.08
698 | Split_Wall_Mounted | Carrier | 42QHA012HSN | Non-Inverter | 1 | 0.96 | 11600 | 979 | 11.8488 | 10100 | 1188 | 8.5017 | 10.09 | Split_Wall_Mounted Carrier 0.96TR SEER 10.09 | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
699 | Split_Wall_Mounted | ZTRUST | TZS30C0 | Non-Inverter | 2 | 2.29 | 27500 | 2270 | 12.1145 | 24200 | 2795 | 8.6583 | 10.31 | Split_Wall_Mounted ZTRUST 2.29TR SEER 10.31 | Split_Wall_Mounted Zamil 2.24TR SEER 10.35
700 | Split_Wall_Mounted | Samsung | AR18JRF3BWKN | Non-Inverter | 1.5 | 1.5 | 18000 | 1540 | 11.6883 | 15500 | 1850 | 8.3784 | 9.94 | Split_Wall_Mounted Samsung 1.5TR SEER 9.94 | Split_Wall_Mounted Chigo 1.38TR SEER 9.88
701 | Split_Wall_Mounted | Gold_Eleteca | GO A245C-1 | Non-Inverter | 2 | 1.9 | 22850 | 1969.82 | 11.6 | 20245 | 2242 | 9.0299 | 10.1 | Split_Wall_Mounted Gold_Eleteca 1.9TR SEER 10.1 | Split_Wall_Mounted Carrier 1.83TR SEER 10.08
702 | Split_Wall_Mounted | LG | B242PC n52 | Non-Inverter | 2 | 1.83 | 22000 | 1900 | 11.5789 | 19000 | 2290 | 8.2969 | 9.85 | Split_Wall_Mounted LG 1.83TR SEER 9.85 | Split_Wall_Mounted LG 1.74TR SEER 9.84
703 | Split_Wall_Mounted | Noon | Nac24kdsfcm | Non-Inverter | 2 | 1.84 | 22100 | 1804 | 12.2506 | 18500 | 2189 | 8.4513 | 10.29 | Split_Wall_Mounted Noon 1.84TR SEER 10.29 | Split_Wall_Mounted Mando 1.84TR SEER 10.28
704 | Split_Wall_Mounted | Craft | DSA20FE7YHA1 | Non-Inverter | 1.5 | 1.48 | 17800 | 1460 | 12.1918 | 15400 | 1820 | 8.4615 | 10.28 | Split_Wall_Mounted Craft 1.48TR SEER 10.28 | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
705 | Split_Wall_Mounted | York | YQFE30YH3CHQO-5 | Non-Inverter | 2 | 2.28 | 27400 | 2238 | 12.2431 | 23200 | 2682 | 8.6503 | 10.36 | Split_Wall_Mounted York 2.28TR SEER 10.36 | Split_Wall_Mounted Zamil 2.24TR SEER 10.35
706 | Split_Wall_Mounted | LG | Y242NCn54 | Non-Inverter | 2 | 1.75 | 20991 | 2200 | 9.5414 | 18251 | 2600 | 7.0196 | 8.18 | Split_Wall_Mounted LG 1.75TR SEER 8.18 | Split_Wall_Mounted LG 1.74TR SEER 8.17
707 | Split_Wall_Mounted | York | HTEA24 OSADR | Non-Inverter | 2 | 2 | 24000 | 2650 | 9.0566 |  |  |  |  | Split_Wall_Mounted York 2TR SEER | Split_Wall_Mounted Carrier 2TR SEER 8.60
708 | Split_Wall_Mounted | General | Assa24futa | Non-Inverter | 2 | 2 | 24000 | 2000 | 12 | 20500 | 2350 | 8.7234 | 10.23 | Split_Wall_Mounted General 2TR SEER 10.23 | Split_Wall_Mounted LG 1.83TR SEER 10.27
709 | Split_Wall_Mounted | LG | B1824C n51 | Non-Inverter | 1.5 | 1.45 | 17500 | 1520 | 11.5132 | 15000 | 1820 | 8.2418 | 9.78 | Split_Wall_Mounted LG 1.45TR SEER 9.78 | Split_Wall_Mounted LG 1.46TR SEER 9.8
710 | Split_Wall_Mounted | ARROW | RO-24SHH | Non-Inverter | 2 | 1.83 | 22000 | 1810 | 12.1547 | 19000 | 2222 | 8.5509 | 10.28 | Split_Wall_Mounted ARROW 1.83TR SEER 10.28 | Split_Wall_Mounted Mando 1.84TR SEER 10.28
711 | Split_Wall_Mounted | Unistar | UNST 30CCG | Non-Inverter | 2 | 2.04 | 24566 | 2100 | 11.6981 | 21154 | 2500 | 8.4616 | 9.97 | Split_Wall_Mounted Unistar 2.04TR SEER 9.97 | Split_Wall_Mounted GREE 2.19TR SEER 10.05
712 | Split_Wall_Mounted | IPX4 | AXO18CV6ROWPK | Non-Inverter | 1.5 | 1.41 | 17000 | 1472 | 11.5489 | 14500 | 1747 | 8.2999 | 9.82 | Split_Wall_Mounted IPX4 1.41TR SEER 9.82 | Split_Wall_Mounted LG 1.46TR SEER 9.8
713 | Split_Wall_Mounted | Zamil | KZC18CSAHIV | Non-Inverter | 1.5 | 1.42 | 17049 | 1790 | 9.5246 | 14497 | 2071 | 7 | 8.15 | Split_Wall_Mounted Zamil 1.42TR SEER 8.15 | Split_Wall_Mounted LG 1.54TR SEER 8.14
714 | Split_Wall_Mounted | Classic | KXC24CSSHIV | Non-Inverter | 2 | 1.95 | 23493 | 2460 | 9.55 | 20104 | 2935 | 6.8497 | 8.12 | Split_Wall_Mounted Classic 1.95TR SEER 8.12 | Split_Wall_Mounted Zamil 1.95TR SEER 8.11
715 | Split_Wall_Mounted | Mando | AC-18C-MP | Non-Inverter | 1.5 | 1.53 | 18400 | 1560 | 11.7949 | 16600 | 1860 | 8.9247 | 10.21 | Split_Wall_Mounted Mando 1.53TR SEER 10.21 | Split_Wall_Mounted Ugine 1.48TR SEER 10.23
716 | Split_Wall_Mounted | LG | S382GH | Non-Inverter | 2.5 | 2.6 | 31236 | 3800 | 8.22 | 27472 | 4220 | 6.51 | 7.19 | Split_Wall_Mounted LG 2.6TR SEER 7.19 | Split_Wall_Mounted LG 2.6TR SEER 7.18
717 | Split_Wall_Mounted | LG | S242HQ | Non-Inverter | 2 | 2 | 24000 | 2600 | 9.2308 | 19654 | 2840 | 6.9204 | 7.91 | Split_Wall_Mounted LG 2TR SEER 7.91 | Split_Wall_Mounted Carrier 1.81TR SEER 7.91
718 | Split_Wall_Mounted | ARROW | AX18C | Non-Inverter | 1.5 | 1.5 | 18000 | 1920 | 9.375 | 16600 | 2350 | 7.0638 | 8.13 | Split_Wall_Mounted ARROW 1.5TR SEER 8.13 | Split_Wall_Mounted LG 1.54TR SEER 8.14
719 | Split_Wall_Mounted | Craft | DSW36FE7HY7M | Non-Inverter | 3 | 2.97 | 35712 | 2951 | 12.1017 |  |  |  |  | Split_Wall_Mounted Craft 2.97TR SEER | Split_Wall_Mounted Carrier 2.75TR SEER 8.81
720 | Split_Wall_Mounted | Craft | DS30FE7HY7WM | Non-Inverter | 2.5 | 2.34 | 28118 | 2342 | 12.006 | 23871 | 2791 | 8.5528 | 10.18 | Split_Wall_Mounted Craft 2.34TR SEER 10.18 | Split_Wall_Mounted Carrier 2.25TR SEER 10.20
721 | Split_Wall_Mounted | LG | X182SH | Non-Inverter | 1.5 | 1.52 | 18255 | 1900 | 9.6079 | 15184 | 2200 | 6.9018 | 8.15 | Split_Wall_Mounted LG 1.52TR SEER 8.15 | Split_Wall_Mounted LG 1.52TR SEER 8.15
722 | Split_Wall_Mounted | Craft | DS24FE7H5Y | Non-Inverter | 2 | 1.86 | 22400 | 2330 | 9.6137 | 20002 | 2700 | 7.4081 | 8.36 | Split_Wall_Mounted Craft 1.86TR SEER 8.36 | Split_Wall_Mounted Carrier 1.79TR SEER 8.31
723 | Split_Wall_Mounted | LG | NT382H2 | Inverter | 2.5 | 2.5 | 30000 | 2440 | 12.2951 | 25400 | 2885 | 8.8042 | 10.44 | Split_Wall_Mounted LG 2.5TR SEER 10.44 | Split_Wall_Mounted LG 2.5TR SEER 10.43
724 | Split_Wall_Mounted | General | GC-30KFC | Non-Inverter | 2 | 2.23 | 26800 | 2161 | 12.4017 |  |  |  |  | Split_Wall_Mounted General 2.23TR SEER | Split_Wall_Mounted Gree 2.25TR SEER 11.11
725 | Split_Wall_Mounted | Craft | DS18CE7H5YHS | Non-Inverter | 1.5 | 1.64 | 19752 | 2003 | 9.8612 | 17289 | 2301 | 7.5137 | 8.53 | Split_Wall_Mounted Craft 1.64TR SEER 8.53 | Split_Wall_Mounted LG 1.5TR SEER 8.40
726 | Split_Wall_Mounted | Zamil | KZC24CSGHIV | Non-Inverter | 2 | 1.83 | 22001 | 2303 | 9.5532 | 18801 | 2686 | 6.9996 | 8.17 | Split_Wall_Mounted Zamil 1.83TR SEER 8.17 | Split_Wall_Mounted Zamil 1.99TR SEER9.77
727 | Split_Wall_Mounted | Zamil | ACSU24 | Non-Inverter | 2 | 1.91 | 23000 | 2770 | 8.3032 |  |  |  |  | Split_Wall_Mounted Zamil 1.91TR SEER | Split_Wall_Mounted Carrier 1.79TR SEER 8.31
728 | Split_Wall_Mounted | Fuji | FJS18CHR | Non-Inverter | 1.5 | 1.38 | 16675 | 1450 | 11.5 | 14362 | 1670 | 8.6 | 9.89 | Split_Wall_Mounted Fuji 1.38TR SEER 9.89 | Split_Wall_Mounted Chigo 1.38TR SEER 9.88
729 | Split_Wall_Mounted | Mando | MP-12CDN | Non-Inverter | 1 | 1 | 12000 | 968 | 12.3967 | 10400 | 1195 | 8.7029 | 10.48 | Split_Wall_Mounted Mando 1TR SEER 10.48 | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
730 | Split_Floor_Standing | Daewoo | DPA-380RH / 300RH | Non-Inverter | 3 | 3.16 | 38000 | 4000 | 9.5 | 31500 | 4500 | 7 | 8.11 | Split_Floor_Standing Daewoo 3.16TR SEER 8.11 | Split_Floor_Standing Daewoo 3.16TR SEER 8.11
731 | Split_Floor_Standing | LG | LPNC452TM5 | Non-Inverter | 3 | 3.33 | 39988.6267 | 4200 | 9.5211 | 34017.6287 | 4970 | 6.8446 | 8.09 | Split_Floor_Standing LG 3.33TR SEER 8.09 | Split_Floor_Standing LG 3.33TR SEER 8.08
732 | Split_Floor_Standing | Zamil | DFX48ESCNASQ | Non-Inverter | 3.5 | 3.41 | 40988.3423 | 5125 | 7.9977 | 34491.8965 | 5725 | 6.0248 | 6.88 | Split_Floor_Standing Zamil 3.41TR SEER 6.88 | Split_Floor_Standing Zamil 3.42TR SEER 6.87
733 | Split_Floor_Standing | Zamil | GFX48MTHNIV | Non-Inverter | 3.5 | 3.5 | 42000 | 4380 | 9.589 | 37530 | 5000 | 7.506 | 8.37 | Split_Floor_Standing Zamil 3.5TR SEER 8.37 | Split_Floor_Standing Zamil 3.5TR SEER 8.37
734 | Split_Floor_Standing | Carrier | 42SD6B.38HK48 | Non-Inverter | 3.5 | 3.54 | 42500 | 4336.7347 | 9.8 | 37000 | 4836.6013 | 7.65 | 8.53 | Split_Floor_Standing Carrier 3.54TR SEER 8.53 | Split_Floor_Standing Carrier 3.54TR SEER 8.52
735 | Split_Floor_Standing | LG | APNQ50GT2E0 | Non-Inverter | 4 | 3.84 | 46096.1046 | 4000 | 11.524 | 39988.6267 | 4750 | 8.4187 | 9.85 | Split_Floor_Standing LG 3.84TR SEER 9.85 | Split_Floor_Standing LG 4TR SEER 10.51
736 | Split_Floor_Standing | Samsung | AF55JV1MAEEX/ AF55JV1MAEEN | Inverter | 4 | 4 | 48000 | 3930 | 12.2137 | 42000 | 4950 | 8.4848 | Inverter | Split_Floor_Standing Samsung 4TR SEER Inverter | Inverter unit "No replacement"
737 | Split_Floor_Standing | LG | APNQ55GT3M4 | Inverter | 4 | 4 | 48000 | 3870 | 12.4031 | 43000 | 4940 | 8.7045 | 10.52 | Split_Floor_Standing LG 4TR SEER 10.52 | Inverter unit "No replacement"
738 | Split_Floor_Standing | LG | LPNC552TM4/TE3 | Non-Inverter | 4 | 4 | 48109 | 5200 | 9.2517 | 42308 | 6150 | 6.8793 | 7.96 | Split_Floor_Standing LG 4TR SEER 7.96 | Split_Floor_Standing LG 4.01TR SEER 7.95
739 | Split_Floor_Standing | LG | LPNC552T1M5/E5 | Non-Inverter | 4 | 4 | 48109.184 | 4750 | 10.1282 | 42308.7859 | 5700 | 7.4226 | 8.68 | Split_Floor_Standing LG 4TR SEER 8.68 | Split_Floor_Standing LG 4.01TR SEER 8.67
740 | Split_Floor_Standing | LG | LPNH552T1M5 | Non-Inverter | 4 | 4 | 48109.184 | 4750 | 10.1282 | 42308.7859 | 5700 | 7.4226 | 8.68 | Split_Floor_Standing LG 4TR SEER 8.68 | Split_Floor_Standing LG 4.01TR SEER 8.67
741 | Split_Floor_Standing | Samsung | APH553QF | Non-Inverter | 4 | 4.16 | 49967.442 | 5200 | 9.6091 | 49967.442 | 5900 | 8.4691 | 8.74 | Split_Floor_Standing Samsung 4.16TR SEER 8.74 | Split_Floor_Standing LG 3.84TR SEER 9.84
742 | Split_Floor_Standing | LG | LP-H652ME0 | Non-Inverter | 4 | 4.35 | 52203.5826 | 6190 | 8.4335 | 42991.1857 | 7440 | 5.7784 | 7.06 | Split_Floor_Standing LG 4.35TR SEER 7.06 | Split_Floor_Standing LG 4.35TR SEER 7.05
743 | Split_Floor_Standing | Zamil | MFZ60CSCDADC | Non-Inverter | 4 | 4.42 | 53056.5823 | 4416 | 12.0146 | 45997.1567 | 5476 | 8.3998 | 10.15 | Split_Floor_Standing Zamil 4.42TR SEER 10.15 | Split_Floor_Standing Zamil 4.421TR SEER 10.15
744 | Split_Floor_Standing | LG | LV-H602LLA3 | Non-Inverter | 4 | 4.49 | 53909.582 | 5600 | 9.6267 | 47426.7842 | 6600 | 7.1859 | 8.29 | Split_Floor_Standing LG 4.49TR SEER 8.29 | Split_Floor_Standing LG 4.49TR SEER 8.28
745 | Split_Floor_Standing | LG | ABUQ60LM3T0 / ABUQ54LM3T0 | Non-Inverter | 4 | 4.5 | 54000 | 4610 | 11.7137 | 45600 | 5300 | 8.6038 | 10.01 | Split_Floor_Standing LG 4.5TR SEER 10.01 | Split_Floor_Standing LG 4.5TR SEER 10.00
746 | Split_Floor_Standing | LG | APNW50GT1M0KR0 | Non-Inverter | 4 | 3.84 | 46188.0342 | 4000 | 11.547 | 39990 | 4750 | 8.4189 | 9.87 | Split_Floor_Standing LG 3.84TR SEER 9.87 | Split_Floor_Standing LG 3.84TR SEER 9.84
747 | Split_Floor_Standing | LG | APNQ55GT3M6 | Inverter | 4 | 4 | 48000 | 3870 | 12.4031 | 43000 | 4940 | 8.7045 | 10.52 | Split_Floor_Standing LG 4TR SEER 10.52 | Inverter unit "No replacement"
748 | Split_Floor_Standing | LG | LPNC552TE3 | Non-Inverter | 4 | 4 | 48111 | 5200 | 9.2521 | 42310 | 6150 | 6.8797 | 7.96 | Split_Floor_Standing LG 4TR SEER 7.96 | Split_Floor_Standing LG 4.01TR SEER 7.95
749 | Split_Floor_Standing | Gree | GVH48AH-D3NTA5A/I | Non-Inverter | 3.5 | 3.62 | 43500 | 3645 | 11.9342 | 38200 | 4495 | 8.4983 | 10.14 | Split_Floor_Standing Gree 3.62TR SEER 10.14 | Split_Floor_Standing Gree 3.62TR SEER 10.14
750 | Split_Floor_Standing | Haam | HM48CFSA21-I | Non-Inverter | 3.5 | 3.58 | 43000 | 3613 | 11.9015 | 38000 | 4524 | 8.3996 | 10.1 | Split_Floor_Standing Haam 3.58TR SEER 10.1 | Split_Floor_Standing Zamil 3.83TR SEER 10.37
751 | Split_Floor_Standing | General | GT48CH | Non-Inverter | 3.5 | 3.61 | 43400 | 3480 | 12.4713 | 37400 | 4210 | 8.8836 | 10.59 | Split_Floor_Standing General 3.61TR SEER 10.59 | Split_Floor_Standing Zamil 3.83TR SEER 10.37
752 | Split_Floor_Standing | LG | LPNC552TE2 | Non-Inverter | 4 | 4.01 | 48205.1282 | 5200 | 9.2702 | 42310 | 6150 | 6.8797 | 7.97 | Split_Floor_Standing LG 4.01TR SEER 7.97 | Split_Floor_Standing LG 4.01TR SEER 7.95
753 | Split_Floor_Standing | Samsung | AF55GC1MBEEN | Non-Inverter | 4 | 3.91 | 47000 | 4500 | 10.4444 | 42000 | 5400 | 7.7778 | 9 | Split_Floor_Standing Samsung 3.91TR SEER 9 | Split_Floor_Standing Samsung 4.16TR SEER 8.74
754 | Split_Floor_Standing | Haas | HHFS50FE6 | Non-Inverter | 4 | 3.86 | 46400 | 3880 | 11.9588 | 40600 | 4740 | 8.5654 | 10.18 | Split_Floor_Standing Haas 3.86TR SEER 10.18 | Split_Floor_Standing Gree 3.62TR SEER 10.14
755 | Split_Floor_Standing | Haas | HHFS50FE7 | Non-Inverter | 3.5 | 3.75 | 45000 | 3780 | 11.9048 | 38560 | 4550 | 8.4747 | 10.1 | Split_Floor_Standing Haas 3.75TR SEER 10.1 | Split_Floor_Standing Gree 3.62TR SEER 10.14
756 | Split_Floor_Standing | LG | LPNH552T1E5 | Non-Inverter | 4 | 4 | 48111 | 4750 | 10.1286 | 42310 | 5700 | 7.4228 | 8.68 | Split_Floor_Standing LG 4TR SEER 8.68 | Split_Floor_Standing LG 4.01TR SEER 8.67
757 | Split_Floor_Standing | Carrier | 38SDL6B | Non-Inverter | 4 | 4 | 48000 | 4100 | 11.7073 | 41500 | 4950 | 8.3838 | 9.95 | Split_Floor_Standing Carrier 4TR SEER 9.95 | Split_Floor_Standing Carrier 4TR SEER 9.95
758 | Split_Floor_Standing | Mando | AC-FS-48000C | Non-Inverter | 4 | 3.85 | 46200 | 3970 | 11.6373 | 41000 | 4920 | 8.3333 | 9.91 | Split_Floor_Standing Mando 3.85TR SEER 9.91 | Split_Floor_Standing LG 4TR SEER 10.51
759 | Split_Floor_Standing | Gree | GVC60AH-H3NTA5A/I | Non-Inverter | 4 | 4.25 | 51000 | 4360 | 11.6972 | 43600 | 5130 | 8.499 | 9.98 | Split_Floor_Standing Gree 4.25TR SEER 9.98 | Split_Floor_Standing Carrier 4TR SEER 9.95
760 | Split_Floor_Standing | Midea | MFTGA50HRN | Non-Inverter | 4 | 3.87 | 46454 | 3759 | 12.3581 | 40818 | 4710 | 8.6662 | 10.46 | Split_Floor_Standing Midea 3.87TR SEER 10.46 | Split_Floor_Standing LG 4TR SEER 10.51
761 | Split_Floor_Standing | Mitsubishi | PSH-6GJS | Non-Inverter | 4 | 4.32 | 51900 | 6250 | 8.304 | 45700 | 7420 | 6.159 | 7.14 | Split_Floor_Standing Mitsubishi 4.32TR SEER 7.14 | Split_Floor_Standing LG 4.35TR SEER 7.05
762 | Split_Floor_Standing | LG | LPNC559T1M5 | Non-Inverter | 4 | 4 | 48101 | 4760 | 10.1053 | 42305 | 5750 | 7.3574 | 8.64 | Split_Floor_Standing LG 4TR SEER 8.64 | Split_Floor_Standing LG 4.01TR SEER 8.67
763 | Split_Floor_Standing | Classic | MFX48CSHNAD | Non-Inverter | 4 | 3.8 | 45600 | 3800 | 12 | 40600 | 4693 | 8.6512 | 10.25 | Split_Floor_Standing Classic 3.8TR SEER 10.25 | Split_Floor_Standing LG 4TR SEER 10.51
764 | Split_Floor_Standing | LG | LPNC552T1M5 | Non-Inverter | 4 | 4 | 48111.2022 | 4750 | 10.1287 | 42310.5608 | 5700 | 7.4229 | 8.68 | Split_Floor_Standing LG 4TR SEER 8.68 | Split_Floor_Standing LG 4.01TR SEER 8.67
765 | Split_Floor_Standing | Samsung | AP55Q1CN | Non-Inverter | 4 | 4.16 | 50000 | 5500 | 9.0909 | 44000 | 6250 | 7.04 | 7.9 | Split_Floor_Standing Samsung 4.16TR SEER 7.9 | Split_Floor_Standing Samsung 4.16TR SEER 8.74
766 | Split_Floor_Standing | Haam | HM48CFSA20 | Non-Inverter | 3.5 | 3.58 | 43000 | 3629 | 11.849 | 38000 | 4524 | 8.3996 | 10.06 | Split_Floor_Standing Haam 3.58TR SEER 10.06 | Split_Floor_Standing Gree 3.62TR SEER 10.14
767 | Split_Floor_Standing | LG | APNQ55GT3MT6 | Inverter | 4 | 4 | 48000 | 3870 | 12.4031 | 43000 | 4940 | 8.7045 | 10.52 | Split_Floor_Standing LG 4TR SEER 10.52 | Inverter unit "No replacement"
768 | Split_Floor_Standing | LG | APNQ50GT2MEO | Non-Inverter | 4 | 3.84 | 46153.8462 | 4000 | 11.5385 | 40000 | 4750 | 8.4211 | 9.86 | Split_Floor_Standing LG 3.84TR SEER 9.86 | Split_Floor_Standing LG 3.84TR SEER 9.84
769 | Split_Floor_Standing | LG | APNQ55GT3M | Non-Inverter | 4 | 4 | 48000 | 3900 | 12.3077 | 45000 | 5170 | 8.7041 | 10.5 | Split_Floor_Standing LG 4TR SEER 10.5 | Split_Floor_Standing LG 4TR SEER 10.51
770 | Split_Floor_Standing | Haas | HHFS150FE6 | Non-Inverter | 4 | 3.83 | 46000 | 3739 | 12.3028 | 38000 | 4510 | 8.4257 | 10.3 | Split_Floor_Standing Haas 3.83TR SEER 10.3 | Split_Floor_Standing Samsung 4TR SEER 10.3
771 | Split_Floor_Standing | Midea | MFTGA50CRN2 | Non-Inverter | 4 | 3.85 | 46200 | 3970 | 11.6373 | 41000 | 4920 | 8.3333 | 9.91 | Split_Floor_Standing Midea 3.85TR SEER 9.91 | Split_Floor_Standing Carrier 4TR SEER 9.95
772 | Split_Floor_Standing | LG | APNQ55GT3MO | Non-Inverter | 4 | 4 | 48000 | 3900 | 12.3077 | 45000 | 5170 | 8.7041 | 10.5 | Split_Floor_Standing LG 4TR SEER 10.5 | Split_Floor_Standing LG 4TR SEER 10.51
773 | Split_Floor_Standing | Samsung | AP55Q0CN | Non-Inverter | 4 | 4.33 | 52000 | 5400 | 9.6296 | 45000 | 6400 | 7.0312 | 8.23 | Split_Floor_Standing Samsung 4.33TR SEER 8.23 | Split_Floor_Standing LG 4.49TR SEER 8.28
774 | Split_Floor_Standing | LG | LPNC55BTM4 | Non-Inverter | 4 | 4 | 48000 | 5400 | 8.8889 | 42310 | 6350 | 6.663 | 7.66 | Split_Floor_Standing LG 4TR SEER 7.66 | Split_Floor_Standing LG 3.72TR SEER 7.65
775 | Split_Floor_Standing | Zamil | MFX48CSHDAD | Non-Inverter | 4 | 3.83 | 46000 | 3833 | 12.001 | 40800 | 4857 | 8.4002 | 10.16 | Split_Floor_Standing Zamil 3.83TR SEER 10.16 | Split_Floor_Standing Zamil 3.83TR SEER 10.37
776 | Split_Floor_Standing | LG | LPUC55BTM4 | Non-Inverter | 4 | 4 | 48069 | 5400 | 8.9017 | 42273 | 6350 | 6.6572 | 7.67 | Split_Floor_Standing LG 4TR SEER 7.67 | Split_Floor_Standing LG 3.72TR SEER 7.65
777 | Split_Floor_Standing | Ugine | UAFSG48H | Non-Inverter | 3.5 | 3.73 | 44800 | 3680 | 12.1739 | 39000 | 4525 | 8.6188 | 10.32 | Split_Floor_Standing Ugine 3.73TR SEER 10.32 | Split_Floor_Standing Samsung 4TR SEER 10.3
778 | Split_Floor_Standing | LG | APUQ55GT3M0 | Non-Inverter | 4 | 4 | 48000 | 3900 | 12.3077 | 45000 | 5170 | 8.7041 | 10.5 | Split_Floor_Standing LG 4TR SEER 10.5 | Split_Floor_Standing LG 4TR SEER 10.51
779 | Split_Floor_Standing | Daewoo | DPA-380RH | Non-Inverter | 3 | 3.16 | 38000 | 4000 | 9.5 | 31500 | 4500 | 7 | 8.11 | Split_Floor_Standing Daewoo 3.16TR SEER 8.11 | Split_Floor_Standing Daewoo 3.16TR SEER 8.11
780 | Split_Floor_Standing | Mando | AC-FS-60000C | Non-Inverter | 4 | 4.35 | 52200 | 4410 | 11.8367 | 45500 | 5470 | 8.3181 | 10.02 | Split_Floor_Standing Mando 4.35TR SEER 10.02 | Split_Floor_Standing LG 4TR SEER 10.51
781 | Split_Floor_Standing | Carrier | 38HFL7B1A | Non-Inverter | 5 | 4.66 | 56000 | 4590 | 12.2004 | 50000 | 5556 | 8.9993 | 10.48 | Split_Floor_Standing Carrier 4.66TR SEER 10.48 | Split_Floor_Standing Zamil 4.421TR SEER 10.15
782 | Split_Floor_Standing | Carrier | 42HFL7B1A | Non-Inverter | 5 | 4.66 | 56000 | 4628 | 12.1003 | 50000 | 5556 | 8.9993 | 10.42 | Split_Floor_Standing Carrier 4.66TR SEER 10.42 | Split_Floor_Standing Zamil 4.421TR SEER 10.15
783 | Split_Floor_Standing | York | YLFE60BZH3CMSR5 | Non-Inverter | 4 | 4.25 | 51000 | 4113 | 12.3997 | 43000 | 5000 | 8.6 | 10.43 | Split_Floor_Standing York 4.25TR SEER 10.43 | Split_Floor_Standing LG 4TR SEER 10.51
784 | Split_Floor_Standing | York | YE8SD55SSCAC41-FT / YE8FT55SC7AC41 | Non-Inverter | 4 | 4.25 | 51000 | 4322 | 11.8001 | 45000 | 5322 | 8.4555 | 10.05 | Split_Floor_Standing York 4.25TR SEER 10.05 | Split_Floor_Standing LG 4.5TR SEER 10.00
785 | Split_Floor_Standing | LG | LP-E50B1CL | Non-Inverter | 4 | 4.16 | 50000 | 5050 | 9.901 |  |  |  |  | Split_Floor_Standing LG 4.16TR SEER | Split_Floor_Standing Carrier 4TR SEER 9.95
786 | Split_Floor_Standing | Samsung | AP55Q1DN | Non-Inverter | 4 | 4.33 | 52000 | 5400 | 9.6296 |  |  |  |  | Split_Floor_Standing Samsung 4.33TR SEER | Split_Floor_Standing Carrier 4TR SEER 9.95
787 | Split_Floor_Standing | Samsung | AP55M0ANUMG | Non-Inverter | 4 | 4.16 | 50000 | 5235 | 9.5511 |  |  |  |  | Split_Floor_Standing Samsung 4.16TR SEER | Split_Floor_Standing LG 3.84TR SEER 9.84
788 | Split_Floor_Standing | Zamil | MFZ48CSHDAD | Non-Inverter | 4 | 3.83 | 45995 | 3740 | 12.2981 | 41000 | 4824 | 8.4992 | 10.38 | Split_Floor_Standing Zamil 3.83TR SEER 10.38 | Split_Floor_Standing LG 4TR SEER 10.51
789 | Split_Floor_Standing | LG | LPNH552TM4 | Non-Inverter | 4 | 3.76 | 45128.2051 | 5150 | 8.7628 | 38898 | 6100 | 6.3767 | 7.48 | Split_Floor_Standing LG 3.76TR SEER 7.48 | Split_Floor_Standing LG 3.75TR SEER 7.47
790 | Split_Floor_Standing | Carrier | 42SDL6B | Non-Inverter | 4 | 4 | 48000 | 4152 | 11.5607 |  |  |  |  | Split_Floor_Standing Carrier 4TR SEER | Split_Floor_Standing LG 4TR SEER 10.51
791 | Split_Floor_Standing | Kelvinator | EQ060SHAA | Non-Inverter | 4 | 4.45 | 53450 | 5626 | 9.5005 | 47571 | 6923 | 6.8714 | 8.12 | Split_Floor_Standing Kelvinator 4.45TR SEER 8.12 | Split_Floor_Standing LG 4.01TR SEER 7.95
792 | Split_Floor_Standing | Haam | FS-050C/hr | Non-Inverter | 4 | 4.16 | 50000 | 5930 | 8.4317 |  |  |  |  | Split_Floor_Standing Haam 4.16TR SEER | Split_Floor_Standing LG 4.49TR SEER 8.28
793 | Split_Floor_Standing | LG | APNQ50GT1M0 | Non-Inverter | 4 | 3.84 | 46098.0384 | 4000 | 11.5245 | 39990.3042 | 4760 | 8.4013 | 9.85 | Split_Floor_Standing LG 3.84TR SEER 9.85 | Split_Floor_Standing LG 3.84TR SEER 9.84
794 | Split_Floor_Standing | Kelvinator | KEQB60SHAC2N | Non-Inverter | 4 | 4.5 | 54000 | 4681 | 11.536 |  |  |  |  | Split_Floor_Standing Kelvinator 4.5TR SEER | Split_Floor_Standing Zamil 4.421TR SEER 10.15
795 | Split_Floor_Standing | LG | APNQ55GT3M2 | Inverter | 4 | 4 | 48000 | 3870 | 12.4031 | 43000 | 4940 | 8.7045 | 10.52 | Split_Floor_Standing LG 4TR SEER 10.52 | Inverter unit "No replacement"
796 | Split_Floor_Standing | Carrier | 42HD6B38HKC48 | Non-Inverter | 3.5 | 3.66 | 44000 | 4900 | 8.9796 |  |  |  |  | Split_Floor_Standing Carrier 3.66TR SEER | Split_Floor_Standing LG 4.01TR SEER 8.67
797 | Split_Floor_Standing | Gree | GVH48AL-D3DTC7A/I | Non-Inverter | 3.5 | 3.73 | 44800 | 3688 | 12.1475 |  |  |  |  | Split_Floor_Standing Gree 3.73TR SEER | Split_Floor_Standing LG 4TR SEER 10.51
798 | Split_Floor_Standing | LG | LP-C55BTM2 | Non-Inverter | 5 | 4.58 | 55000 | 5050 | 10.8911 |  |  |  |  | Split_Floor_Standing LG 4.58TR SEER | Split_Floor_Standing Zamil 4.421TR SEER 10.15
799 | Split_Floor_Standing | Gree | GVH48AH-D3NTA5A/O | Non-Inverter | 3.5 | 3.62 | 43500 | 3645 | 11.9342 | 38200 | 4495 | 8.4983 | 10.14 | Split_Floor_Standing Gree 3.62TR SEER 10.14 | Split_Floor_Standing Gree 3.62TR SEER 10.14
800 | Split_Floor_Standing | LG | LPNC552TM4 | Non-Inverter | 3.5 | 3.72 | 44699 | 5200 | 8.596 | 42310 | 6150 | 6.8797 | 7.59 | Split_Floor_Standing LG 3.72TR SEER 7.59 | Split_Floor_Standing Samsung 4TR SEER 10.3
801 | Split_Floor_Standing | Carrier | 38HD48-3-CT | Non-Inverter | 4 | 4 | 48000 | 4152 | 11.5607 |  |  |  |  | Split_Floor_Standing Carrier 4TR SEER | Split_Floor_Standing LG 4TR SEER 10.51
802 | Split_Ceiling_Ducted | LG | LBNC422GSA4 | Non-Inverter | 3.5 | 3.37 | 40500.4265 | 5050 | 8.0199 | 36508.3878 | 5750 | 6.3493 | 7.03 | Split_Ceiling_Ducted LG 3.37TR SEER 7.03 | Split_Ceiling_Ducted LG 3.37TR SEER 7.02
803 | Split_Ceiling_Ducted | Zamil | KYA060H/DYA60H | Non-Inverter | 4 | 4.41 | 53000 | 4600 | 11.5217 | 47200 | 5690 | 8.2953 | 9.83 | Split_Ceiling_Ducted Zamil 4.41TR SEER 9.83 | Split_Ceiling_Ducted Zamil 4.41TR SEER 9.83
804 | Split_Ceiling_Ducted | Carrier | 38MKS60US30-01 | Non-Inverter | 4 | 4.45 | 53500 | 5490 | 9.745 | 47000 | 6710 | 7.0045 | 8.31 | Split_Ceiling_Ducted Carrier 4.45TR SEER 8.31 | Split_Ceiling_Ducted Carrier 4.45TR SEER 8.30
805 | Split_Ceiling_Ducted | LG | LBNC602RSA4 | Non-Inverter | 5 | 4.86 | 58345.1806 | 6350 | 9.1882 | 51214.1029 | 7500 | 6.8285 | 7.9 | Split_Ceiling_Ducted LG 4.86TR SEER 7.9 | Split_Ceiling_Ducted LG 4.86TR SEER 7.90
806 | Split_Ceiling_Ducted | York | YE3SD18OSHBW22-VH | Non-Inverter | 1.5 | 1.5 | 18000 | 2390 | 7.5314 | 15480 | 2850 | 5.4316 | 6.42 | Split_Ceiling_Ducted York 1.5TR SEER 6.42 | Split_Ceiling_Ducted YORK 1.5TR SEER 6.41
807 | Split_Ceiling_Ducted | York | YE3SD48SECAC22-H | Non-Inverter | 4 | 4 | 48000 | 6380 | 7.5235 | 41280 | 5570 | 7.4111 | 6.91 | Split_Ceiling_Ducted York 4TR SEER 6.91 | Split_Ceiling_Ducted YORK 4TR SEER 6.90
808 | Split_Ceiling_Ducted | York | YE3SD30RSHAC22-H | Non-Inverter | 2.5 | 2.5 | 30000 | 3990 | 7.5188 | 25800 | 4750 | 5.4316 | 6.41 | Split_Ceiling_Ducted York 2.5TR SEER 6.41 | Split_Ceiling_Ducted YORK 2.5TR SEER 6.40
809 | Split_Ceiling_Ducted | York | YE3SD36RSHAD22-2 | Non-Inverter | 3 | 3 | 36000 | 4790 | 7.5157 | 30960 | 4750 | 6.5179 | 6.71 | Split_Ceiling_Ducted York 3TR SEER 6.71 | Split_Ceiling_Ducted YORK 3TR SEER 6.70
810 | Split_Ceiling_Ducted | York | YE3SD60SECBK22-H | Non-Inverter | 5 | 5 | 60000 | 7980 | 7.5188 | 51600 | 9540 | 5.4088 | 6.4 | Split_Ceiling_Ducted York 5TR SEER 6.4 | Split_Ceiling_Ducted YORK 5TR SEER 6.39
811 | Split_Ceiling_Cassette | Carrier | 42KTD018HS | Non-Inverter | 1.5 | 1.33 | 16000 | 1330 | 12.0301 | 15000 | 1610 | 9.3168 | 10.52 | Split_Ceiling_Cassette Carrier 1.33TR SEER 10.52 | Split_Ceiling_Cassette Carrier 1.33TR SEER 10.51
812 | Split_Ceiling_Cassette | LG | LT-C182ELE0 | Non-Inverter | 1.5 | 1.5 | 18000 | 1970 | 9.1371 | 16002.2747 | 2150 | 7.4429 | 8.05 | Split_Ceiling_Cassette LG 1.5TR SEER 8.05 | Split_Ceiling_Cassette LG 1.5TR SEER 8.05
813 | Split_Ceiling_Cassette | Mitsubishi | FDTN257HEPA | Non-Inverter | 2 | 1.76 | 21154.3929 | 2680 | 7.8934 | 17742.3941 | 3050 | 5.8172 | 6.75 | Split_Ceiling_Cassette Mitsubishi 1.76TR SEER 6.75 | Split_Ceiling_Cassette Mitsubishi 1.76TR SEER 6.74
814 | Split_Ceiling_Cassette | LG | ATNQ24GPLT2 | Inverter | 2 | 1.83 | 22000 | 1770 | 12.4294 | 20000 | 2260 | 8.8496 | 10.59 | Split_Ceiling_Cassette LG 1.83TR SEER 10.59 | Inverter unit "No replacement"
815 | Split_Ceiling_Cassette | Zamil | SCZ24CHAXCD1 | Non-Inverter | 2 | 1.94 | 23300 | 1900 | 12.2632 | 19800 | 2300 | 8.6087 | 10.36 | Split_Ceiling_Cassette Zamil 1.94TR SEER 10.36 | Split_Ceiling_Cassette Zamil 1.94TR SEER 10.35
816 | Split_Ceiling_Cassette | Carrier | 42KTD024HS | Non-Inverter | 2 | 1.95 | 23500 | 1950 | 12.0513 | 20000 | 2300 | 8.6957 | 10.25 | Split_Ceiling_Cassette Carrier 1.95TR SEER 10.25 | Split_Ceiling_Cassette Carrier 1.96TR SEER 10.25
817 | Split_Ceiling_Cassette | Carrier | 42QTD024HSN | Non-Inverter | 2 | 1.96 | 23600 | 1927 | 12.247 | 20000 | 2300 | 8.6957 | 10.37 | Split_Ceiling_Cassette Carrier 1.96TR SEER 10.37 | Split_Ceiling_Cassette Carrier 1.97TR SEER 10.37
818 | Split_Ceiling_Cassette | LG | LTNC242PLE1 | Non-Inverter | 2 | 1.99 | 23885 | 2500 | 9.554 | 21667 | 3050 | 7.1039 | 8.24 | Split_Ceiling_Cassette LG 1.99TR SEER 8.24 | Split_Ceiling_Cassette LG 1.99TR SEER 8.23
819 | Split_Ceiling_Cassette | LG | LT-C242ELE0 | Non-Inverter | 2 | 2 | 24000 | 2500 | 9.6 | 21000 | 2830 | 7.4205 | 8.34 | Split_Ceiling_Cassette LG 2TR SEER 8.34 | Split_Ceiling_Cassette LG 2.0TR SEER 8.33
820 | Split_Ceiling_Cassette | Mitsubishi | FDTN306CEP | Non-Inverter | 2 | 2.01 | 24225.1919 | 3030 | 7.9951 | 19448.3935 | 3260 | 5.9658 | 6.83 | Split_Ceiling_Cassette Mitsubishi 2.01TR SEER 6.83 | Split_Ceiling_Cassette Mitsubishi 2.02TR SEER 6.93
821 | Split_Ceiling_Cassette | LG | LTNC302PLEO | Non-Inverter | 2.5 | 2.31 | 27800 | 3240 | 8.5802 | 24400 | 3800 | 6.4211 | 7.39 | Split_Ceiling_Cassette LG 2.31TR SEER 7.39 | Split_Ceiling_Cassette LG 2.32TR SEER 8.12
822 | Split_Ceiling_Cassette | LG | LTNC302NLE1 | Non-Inverter | 2.5 | 2.31 | 27807.7907 | 2920 | 9.5232 | 24429.9119 | 3550 | 6.8817 | 8.13 | Split_Ceiling_Cassette LG 2.31TR SEER 8.13 | Split_Ceiling_Cassette LG 2.32TR SEER 8.12
823 | Split_Ceiling_Cassette | Carrier | 42KTD036HS | Non-Inverter | 3 | 2.87 | 34500 | 2950 | 11.6949 | 31000 | 3600 | 8.6111 | 10.05 | Split_Ceiling_Cassette Carrier 2.87TR SEER 10.05 | Split_Ceiling_Cassette Carrier 2.88TR SEER 10.05
824 | Split_Ceiling_Cassette | LG | ATUW48GMLT0SA0 | Non-Inverter | 4 | 3.83 | 45993.7447 | 3960 | 11.6146 | 39067.387 | 4660 | 8.3836 | 9.88 | Split_Ceiling_Cassette LG 3.83TR SEER 9.88 | Split_Ceiling_Cassette LG 3.83TR SEER 9.87
825 | Split_Ceiling_Cassette | LG | LTUH602MLE0 | Non-Inverter | 4 | 4.21 | 50634.0631 | 5500 | 9.2062 | 41967.586 | 6700 | 6.2638 | 7.7 | Split_Ceiling_Cassette LG 4.21TR SEER 7.7 | Split_Ceiling_Cassette LG 4.21TR SEER 7.69
826 | Split_Ceiling_Cassette | Mando | AC-CST-48000H | Non-Inverter | 3.5 | 3.75 | 45000 | 3850 | 11.6883 | 38500 | 4640 | 8.2974 | 9.91 | Split_Ceiling_Cassette Mando 3.75TR SEER 9.91 | Split_Ceiling_Cassette LG 3.83TR SEER 9.87
827 | Split_Ceiling_Cassette | Zamil | SCX36CHAXCD | Non-Inverter | 3 | 2.83 | 34000 | 2800 | 12.1429 | 28400 | 3350 | 8.4776 | 10.23 | Split_Ceiling_Cassette Zamil 2.83TR SEER 10.23 | Split_Ceiling_Cassette Carrier 2.88TR SEER 10.05
828 | Split_Ceiling_Cassette | LG | LTNH482MLE0 | Non-Inverter | 3.5 | 3.74 | 44972 | 4650 | 9.6714 | 39103 | 6740 | 5.8016 | 7.82 | Split_Ceiling_Cassette LG 3.74TR SEER 7.82 | Split_Ceiling_Cassette LG 3.83TR SEER 9.87
829 | Split_Ceiling_Cassette | LG | LTUO302PIE0 | Non-Inverter | 2.5 | 2.32 | 27955 | 3210 | 8.7087 | 24567 | 3800 | 6.465 | 7.49 | Split_Ceiling_Cassette LG 2.32TR SEER 7.49 | Split_Ceiling_Cassette LG 2.31TR SEER 7.39
830 | Split_Ceiling_Cassette | LG | LTUC242QLE0 | Non-Inverter | 2 | 1.76 | 21137 | 2470 | 8.5575 | 18766 | 2900 | 6.471 | 7.4 | Split_Ceiling_Cassette LG 1.76TR SEER 7.4 | Split_Ceiling_Cassette LG 1.83TR SEER 10.59
831 | Split_Ceiling_Cassette | LG | LTUC362NLE0 | Non-Inverter | 3 | 2.74 | 32995 | 3900 | 8.4603 | 29310 | 4500 | 6.5133 | 7.35 | Split_Ceiling_Cassette LG 2.74TR SEER 7.35 | Split_Ceiling_Cassette Carrier 2.88TR SEER 10.05
832 | Split_Ceiling_Cassette | LG | LTUH362NLE0 | Non-Inverter | 3 | 2.74 | 32997.37 | 3900 | 8.4609 | 29338 | 4500 | 6.5196 | 7.35 | Split_Ceiling_Cassette LG 2.74TR SEER 7.35 | Split_Ceiling_Cassette Carrier 2.88TR SEER 10.05
833 | Split_Ceiling_Cassette | LG | LT-H2442EL1EO | Non-Inverter | 2 | 2 | 24000 | 2500 | 9.6 | 20984.6733 | 2830 | 7.4151 | 8.34 | Split_Ceiling_Cassette LG 2TR SEER 8.34 | Split_Ceiling_Cassette LG 2.0TR SEER 8.33
834 | Split_Ceiling_Cassette | Gree | GUD18T1/A2-S | Non-Inverter | 1.5 | 1.51 | 18200 | 1470 | 12.381 | 16800 | 2000 | 8.4 | 10.42 | Split_Ceiling_Cassette Gree 1.51TR SEER 10.42 | Split_Ceiling_Cassette Carrier 1.33TR SEER 10.51
835 | Split_Ceiling_Cassette | LG | LBUH602RSA4 | Non-Inverter | 5 | 4.86 | 58347.6282 | 6350 | 9.1886 | 48964.2377 | 7680 | 6.3756 | 7.73 | Split_Ceiling_Cassette LG 4.86TR SEER 7.73 | Split_Ceiling_Cassette LG 4.21TR SEER 7.69
836 | Split_Ceiling_Cassette | LG | LTUC302PLE0 | Non-Inverter | 2.5 | 2.31 | 27801 | 3240 | 8.5806 | 24436 | 3800 | 6.4305 | 7.4 | Split_Ceiling_Cassette LG 2.31TR SEER 7.4 | Split_Ceiling_Cassette LG 2.31TR SEER 7.39
837 | Split_Ceiling_Cassette | LG | LBUH482RSA4 | Non-Inverter | 4 | 4 | 47992.82 | 5040 | 9.5224 | 42517.48 | 6200 | 6.8577 | 8.13 | Split_Ceiling_Cassette LG 4TR SEER 8.13 | Split_Ceiling_Cassette LG 4.21TR SEER 7.69
838 | Split_Ceiling_Cassette | LG | ATNW24GNLT0 | Non-Inverter | 2 | 1.99 | 23985 | 2070 | 11.587 | 19895 | 2070 | 9.6111 | 10.19 | Split_Ceiling_Cassette LG 1.99TR SEER 10.19 | Split_Ceiling_Cassette Carrier 1.96TR SEER 10.25
839 | Split_Ceiling_Cassette | Gree | GUHD36TS3CO | Inverter | 2.5 | 2.66 | 32000 | 2760 | 11.5942 | 26500 | 3190 | 8.3072 | 9.83 | Split_Ceiling_Cassette Gree 2.66TR SEER 9.83 | Inverter unit "No replacement"
840 | Split_Ceiling_Cassette | Ugine | UC-18K-C-1 | Non-Inverter | 1.5 | 1.36 | 16400 | 1900 | 8.6316 | 15300 | 2200 | 6.9545 | 7.62 | Split_Ceiling_Cassette Ugine 1.36TR SEER 7.62 | Split_Ceiling_Cassette LG 1.5TR SEER 8.05
841 | Split_Ceiling_Cassette | Craft | DS24CE7HY7KM | Non-Inverter | 2 | 1.93 | 23200 | 1933 | 12.0021 | 20000 | 2353 | 8.4998 | 10.17 | Split_Ceiling_Cassette Craft 1.93TR SEER 10.17 | Split_Ceiling_Cassette Carrier 1.96TR SEER 10.25
842 | Split_Ceiling_Cassette | LG | S322GHSD3 | Non-Inverter | 2 | 2.2 | 26478.2219 | 3050 | 8.6814 | 23270.8084 | 3570 | 6.5184 | 7.49 | Split_Ceiling_Cassette LG 2.2TR SEER 7.49 | Split_Ceiling_Cassette LG 2.31TR SEER 7.39
843 | Split_Ceiling_Cassette | Samsung | CC36BTVA1 | Non-Inverter | 2.5 | 2.66 | 32000 | 3300 | 9.697 | 28000 | 3650 | 7.6712 | 8.47 | Split_Ceiling_Cassette Samsung 2.66TR SEER 8.47 | Split_Ceiling_Cassette Carrier 2.88TR SEER 10.05
844 | Split_Ceiling_Cassette | LG | LT-H242ELE0 | Non-Inverter | 2 | 2 | 24000 | 2500 | 9.6 | 20991 | 2830 | 7.4173 | 8.34 | Split_Ceiling_Cassette LG 2TR SEER 8.34 | Split_Ceiling_Cassette LG 2.0TR SEER 8.33
845 | Split_Ceiling_Cassette | Zamil | SCX36HAXCD | Non-Inverter | 3 | 2.83 | 34000 | 2800 | 12.1429 | 28400 | 3350 | 8.4776 | 10.23 | Split_Ceiling_Cassette Zamil 2.83TR SEER 10.23 | Split_Ceiling_Cassette Carrier 2.88TR SEER 10.05
846 | Split_Ceiling_Cassette | LG | LTUH242QLE0 | Non-Inverter | 2 | 1.75 | 21059 | 2470 | 8.5259 | 19005 | 2900 | 6.5534 | 7.42 | Split_Ceiling_Cassette LG 1.75TR SEER 7.42 | Split_Ceiling_Cassette LG 1.75TR SEER 7.36
847 | Split_Ceiling_Cassette | LG | ATUW24GNT0 | Non-Inverter | 2 | 2 | 24034.188 | 2070 | 11.6107 | 19892 | 2070 | 9.6097 | 10.21 | Split_Ceiling_Cassette LG 2TR SEER 10.21 | Split_Ceiling_Cassette Carrier 1.96TR SEER 10.25
848 | Split_Ceiling_Cassette | Gree | GWC24ACE-C | Non-Inverter | 2 | 1.83 | 22000 | 1880 | 11.7021 | 18700 | 2255 | 8.2927 | 9.91 | Split_Ceiling_Cassette Gree 1.83TR SEER 9.91 | Split_Ceiling_Cassette Carrier 1.96TR SEER 10.25
849 | Split_Ceiling_Cassette | Carrier | 38QGJ024-323F | Non-Inverter | 2 | 2 | 24000 | 2770 | 8.6643 |  |  |  |  | Split_Ceiling_Cassette Carrier 2TR SEER | Split_Ceiling_Cassette LG 2.0TR SEER 8.33
850 | Split_Ceiling_Cassette | LG | LTNC242QLE0 | Non-Inverter | 2 | 1.75 | 21018.7947 | 2470 | 8.5096 | 18698.5382 | 2900 | 6.4478 | 7.36 | Split_Ceiling_Cassette LG 1.75TR SEER 7.36 | Split_Ceiling_Cassette LG 1.75TR SEER 7.36
851 | Split_Ceiling_Cassette | LG | LT-C302FLE0 | Non-Inverter | 2.5 | 2.5 | 30000 | 2980 | 10.0671 |  |  |  |  | Split_Ceiling_Cassette LG 2.5TR SEER | Split_Ceiling_Cassette LG 2.32TR SEER 8.12
852 | Split_Ceiling_Cassette | Gree | GUTD24PHS1/A-S(S) | Non-Inverter | 2.5 | 2.5 | 30000 | 2890 | 10.3806 |  |  |  |  | Split_Ceiling_Cassette Gree 2.5TR SEER | Split_Ceiling_Cassette LG 2.32TR SEER 8.12
853 | Split_Ceiling_Cassette | Mando | Model1.1MADO | Non-Inverter | 2 | 1.75 | 21059.8291 | 2470 | 8.5262 |  |  |  |  | Split_Ceiling_Cassette Mando 1.75TR SEER | Split_Ceiling_Cassette LG 1.75TR SEER 7.36
854 | Split_Ceiling_Cassette | General | AOS24AAWF | Non-Inverter | 2 | 2 | 24034.188 | 2070 | 11.6107 |  |  |  |  | Split_Ceiling_Cassette General 2TR SEER | Split_Ceiling_Cassette LG 1.83TR SEER 10.59
855 | Split_Ceiling_Cassette | LG | LV-B2421HL | Non-Inverter | 2 | 2 | 24000 | 2560 | 9.375 |  |  |  |  | Split_Ceiling_Cassette LG 2TR SEER | Split_Ceiling_Cassette Carrier 1.96TR SEER 10.25
856 | Split_Ceiling_Cassette | LG | LTUH302PLE | Non-Inverter | 2.5 | 2.5 | 30000 | 2980 | 10.0671 |  |  |  |  | Split_Ceiling_Cassette LG 2.5TR SEER | Split_Ceiling_Cassette LG 2.32TR SEER 8.12
857 | Split_Ceiling_Cassette | LG | LS-T242CBG-C | Non-Inverter | 2 | 2 | 24000 | 2525 | 9.505 |  |  |  |  | Split_Ceiling_Cassette LG 2TR SEER | Split_Ceiling_Cassette Carrier 1.96TR SEER 10.25
858 | Split_Ceiling_Cassette | Carrier | 38hkc60ds20-02 | Non-Inverter | 5 | 5 | 60000 | 6200 | 9.6774 |  |  |  |  | Split_Ceiling_Cassette Carrier 5TR SEER | Split_Ceiling_Cassette LG 4.21TR SEER 7.69
859 | Split_Ceiling_Cassette | Carrier | Wcs036HGIR1T-C | Non-Inverter | 2.5 | 2.66 | 32000 | 2760 | 11.5942 | 25000 | 3010 | 8.3056 | 9.78 | Split_Ceiling_Cassette Carrier 2.66TR SEER 9.78 | Split_Ceiling_Cassette Carrier 2.88TR SEER 10.05
860 | Split_Ceiling_Cassette | Carrier | 42QTDA6024VS | Non-Inverter | 2 | 2.25 | 27000 | 2250 | 12 | 24000 | 2810 | 8.5409 | 10.21 | Split_Ceiling_Cassette Carrier 2.25TR SEER 10.21 | Split_Ceiling_Cassette LG 2.32TR SEER 8.12
861 | Split_Ceiling_Cassette | Carrier | 42TNH0362002303 | Non-Inverter | 3 | 2.75 | 33000 | 4204 | 7.8497 |  |  |  |  | Split_Ceiling_Cassette Carrier 2.75TR SEER | Split_Ceiling_Cassette Carrier 2.88TR SEER 10.05
862 | Window | Zamil | PCB19CKXQIMNW | Non-Inverter | 1.5 | 1.52 | 18260 | 2360 | 7.7373 | 14260 | 2600 | 5.4846 | 6.51 | Window Zamil 1.52TR SEER 6.51 | Window LG 1.5TR SEER 7.70
863 | Split_Wall_Mounted | York | YE6SD320SCYW41 / YE6HC32SC7AC41 | Non-Inverter | 2.5 | 2.43 | 29225 | 2532 | 11.5423 | 25893 | 3112 | 8.3204 | 9.85 | Split_Wall_Mounted York 2.43TR SEER 9.85 | Split_Wall_Mounted LG 2.5TR SEER 10.43
864 | Split_Wall_Mounted | General | YE3HW30SH7AC22 / YE3SD30RSHYW22 | Non-Inverter | 2.5 | 2.5 | 30000 | 3990 | 7.5188 | 25800 | 4750 | 5.4316 | 6.41 | Split_Wall_Mounted General 2.5TR SEER 6.41 | Split_Wall_Mounted Royal Temp 2.5TR SEER 7.53
865 | Split_Wall_Mounted | LG | BC36CCL | Non-Inverter | 2.5 | 2.53 | 30400 | 2500 | 12.16 |  |  |  |  | Split_Wall_Mounted LG 2.53TR SEER | Split_Wall_Mounted Carrier 2.58TR SEER 10.41
866 | Window | Carrier | CACH19K5 | Non-Inverter | 1.5 | 1.55 | 18600 | 2450 | 7.5918 | 15200 | 2830 | 5.371 | 6.41 | Window Carrier 1.55TR SEER 6.41 | Window Zamil 1.5TR SEER 6.51
867 | Window | Falcon | FCW19 | Non-Inverter | 1.5 | 1.55 | 18600 | 2450 | 7.5918 |  |  |  |  | Window Falcon 1.55TR SEER | Window LG 1.5TR SEER 7.70
868 | Window | Falcon | FCWH 19K5 | Non-Inverter | 1.5 | 1.55 | 18600 | 2450 | 7.5918 |  |  |  |  | Window Falcon 1.55TR SEER | Window LG 1.5TR SEER 7.70
869 | Window | Haas | HO19E8J | Non-Inverter | 1.5 | 1.54 | 18500 | 2450 | 7.551 |  |  |  |  | Window Haas 1.54TR SEER | Window LG 1.5TR SEER 7.70
870 | Split_Wall_Mounted | Speed_Cool | SC-CCR24SHCZWXS | Non-Inverter | 2 | 2 | 24000 | 3190 | 7.5235 | 20640 | 3820 | 5.4031 | 6.4 | Split_Wall_Mounted Speed_Cool 2TR SEER 6.4 | Split_Wall_Mounted Zamil 2TR SEER 6.69
871 | Split_Wall_Mounted | Speed_Cool | SC-EXGA24SHBC-1S | Non-Inverter | 2 | 2 | 24000 | 3190 | 7.5235 | 20640 | 3820 | 5.4031 | 6.4 | Split_Wall_Mounted Speed_Cool 2TR SEER 6.4 | Split_Wall_Mounted Zamil 2TR SEER 6.69
872 | Split_Wall_Mounted | Kelvinator | KIZB24SH | Non-Inverter | 2 | 2 | 24000 | 3190 | 7.5235 | 20640 | 3820 | 5.4031 | 6.4 | Split_Wall_Mounted Kelvinator 2TR SEER 6.4 | Split_Wall_Mounted Zamil 1.83TR SEER 7.51
873 | Split_Wall_Mounted | Speed_Cool | SC-CCR24HCZWXS | Non-Inverter | 2 | 2 | 24000 | 3190 | 7.5235 | 20640 | 3820 | 5.4031 | 6.4 | Split_Wall_Mounted Speed_Cool 2TR SEER 6.4 | Split_Wall_Mounted Zamil 2TR SEER 6.69
874 | Split_Wall_Mounted | York | YE3HW24SH7AC22 | Non-Inverter | 2 | 2 | 24000 | 3190 | 7.5235 | 20640 | 3820 | 5.4031 | 6.4 | Split_Wall_Mounted York 2TR SEER 6.4 | Split_Wall_Mounted Zamil 2TR SEER 6.69
875 | Split_Wall_Mounted | York | YE3HW18SH7BC22 | Non-Inverter | 1.5 | 1.5 | 18000 | 2390 | 7.5314 | 15480 | 2850 | 5.4316 | 6.42 | Split_Wall_Mounted York 1.5TR SEER 6.42 | Split_Wall_Mounted LG 1.41TR SEER 6.94
876 | Split_Wall_Mounted | York | YE3HW30SH7AC22 | Non-Inverter | 2.5 | 2.5 | 30000 | 3990 | 7.5188 | 25800 | 4750 | 5.4316 | 6.41 | Split_Wall_Mounted York 2.5TR SEER 6.41 | Split_Wall_Mounted Royal Temp 2.5TR SEER 7.53
877 | Split_Wall_Mounted | LG | S3024HNV0 | Non-Inverter | 2.5 | 2.33 | 27989 | 3450 | 8.1128 | 26478 | 4000 | 6.6195 | 7.2 | Split_Wall_Mounted LG 2.33TR SEER 7.2 | Split_Wall_Mounted Zamil 2.11TR SEER7.24
878 | Split_Wall_Mounted | Speed_Cool | SC-EXGA24SHBCIS | Non-Inverter | 2 | 2 | 24000 | 3190 | 7.5235 | 20640 | 3820 | 5.4031 | 6.4 | Split_Wall_Mounted Speed_Cool 2TR SEER 6.4 | Split_Wall_Mounted Zamil 2TR SEER 6.69
879 | Split_Wall_Mounted | LG | S3224C | Non-Inverter | 2.5 | 2.47 | 29685.6354 | 3600 | 8.246 | 25932.2792 | 4200 | 6.1744 | 7.1 | Split_Wall_Mounted LG 2.47TR SEER 7.1 | Split_Wall_Mounted Royal Temp 2.5TR SEER 7.53
880 | Split_Wall_Mounted | Pearl | EZA30SHACL | Non-Inverter | 2.5 | 2.5 | 30000 | 3984 | 7.5301 | 25800 | 4750 | 5.4316 | 6.41 | Split_Wall_Mounted Pearl 2.5TR SEER 6.41 | Split_Wall_Mounted Royal Temp 2.5TR SEER 7.53
881 | Split_Wall_Mounted | Gree | GWH18MC-DINTA8A/I | Non-Inverter | 1.5 | 1.5 | 18083 | 2220 | 8.1455 | 15695 | 2700 | 5.813 | 6.92 | Split_Wall_Mounted Gree 1.5TR SEER 6.92 | Split_Wall_Mounted LG 1.41TR SEER 6.94
882 | Split_Wall_Mounted | York | YE3SD180SHBW22-2 | Non-Inverter | 2 | 2 | 24000 | 3190 | 7.5235 | 20640 | 3820 | 5.4031 | 6.4 | Split_Wall_Mounted York 2TR SEER 6.4 | Split_Wall_Mounted Zamil 2TR SEER 6.69
883 | Split_Wall_Mounted | Speed_Cool | SC-EXGA24HBC1S | Non-Inverter | 2 | 2 | 24000 | 3190 | 7.5235 | 20640 | 3820 | 5.4031 | 6.4 | Split_Wall_Mounted Speed_Cool 2TR SEER 6.4 | Split_Wall_Mounted Zamil 2TR SEER 6.69
884 | Split_Wall_Mounted | Speed_Cool | SC-EXGA24SHBC1S | Non-Inverter | 2 | 2 | 24000 | 3190 | 7.5235 | 20640 | 3820 | 5.4031 | 6.4 | Split_Wall_Mounted Speed_Cool 2TR SEER 6.4 | Split_Wall_Mounted Zamil 2TR SEER 6.69
885 | Split_Wall_Mounted | Speed_Cool | SC-EXGA24SHBC | Non-Inverter | 2 | 2 | 24000 | 3190 | 7.5235 | 20640 | 3820 | 5.4031 | 6.4 | Split_Wall_Mounted Speed_Cool 2TR SEER 6.4 | Split_Wall_Mounted Zamil 1.83TR SEER 7.51
886 | Split_Wall_Mounted | Speed_Cool | SC-EXGA243HBC | Non-Inverter | 2 | 2 | 24000 | 3190 | 7.5235 | 20640 | 3820 | 5.4031 | 6.4 | Split_Wall_Mounted Speed_Cool 2TR SEER 6.4 | Split_Wall_Mounted Zamil 2TR SEER 6.69
887 | Split_Wall_Mounted | Kleenair | KT3F-51G | Non-Inverter | 1.5 | 1.45 | 17400 | 2190 | 7.9452 | 15300 | 2550 | 6 | 6.86 | Split_Wall_Mounted Kleenair 1.45TR SEER 6.86 | Split_Wall_Mounted LG 1.41TR SEER 6.94
888 | Split_Wall_Mounted | PEARL | CCT24PHCZWS | Non-Inverter | 2 | 2 | 24000 | 3190 | 7.5235 | 20640 | 3820 | 5.4031 | 6.4 | Split_Wall_Mounted PEARL 2TR SEER 6.4 | Split_Wall_Mounted Zamil 2TR SEER 6.69
889 | Split_Wall_Mounted | York | YE3SD180SHZW22 | Non-Inverter | 1.5 | 1.5 | 18000 | 2390 | 7.5314 | 15480 | 2850 | 5.4316 | 6.42 | Split_Wall_Mounted York 1.5TR SEER 6.42 | Split_Wall_Mounted LG 1.41TR SEER 6.94
890 | Split_Wall_Mounted | York | YE3SD240SHZW22 | Non-Inverter | 2 | 2 | 24000 | 3191 | 7.5212 | 20640 | 3820 | 5.4031 | 6.4 | Split_Wall_Mounted York 2TR SEER 6.4 | Split_Wall_Mounted Zamil 2TR SEER 6.69
891 | Split_Wall_Mounted | Gree | GWH18MC-D1NTA | Non-Inverter | 1.5 | 1.5 | 18083 | 2220 | 8.1455 | 15695 | 2700 | 5.813 | 6.92 | Split_Wall_Mounted Gree 1.5TR SEER 6.92 | Split_Wall_Mounted LG 1.46TR SEER 9.8
892 | Split_Wall_Mounted | York | YE3SD240SHZW22 / YE3HW24SH7AC22 | Non-Inverter | 2 | 2 | 24000 | 3100 | 7.7419 | 20640 | 3820 | 5.4031 | 6.54 | Split_Wall_Mounted York 2TR SEER 6.54 | Split_Wall_Mounted Zamil 2TR SEER 6.69
893 | Split_Wall_Mounted | York | YE3SD180SHZW22 / YE3HW18SH7BC22 | Non-Inverter | 1.5 | 1.5 | 18000 | 2390 | 7.5314 | 15480 | 2850 | 5.4316 | 6.42 | Split_Wall_Mounted York 1.5TR SEER 6.42 | Split_Wall_Mounted LG 1.41TR SEER 6.94
894 | Split_Wall_Mounted | York | YE3HC30SH7AC22 / YE3SD30RSHYW22 | Non-Inverter | 2.5 | 2.5 | 30000 | 3990 | 7.5188 | 25800 | 4750 | 5.4316 | 6.41 | Split_Wall_Mounted York 2.5TR SEER 6.41 | Split_Wall_Mounted Royal Temp 2.5TR SEER 7.53
895 | Split_Floor_Standing | York | YE3SD60SEHAA22 / YE3FS60SH7AA22 | Non-Inverter | 5 | 5 | 60000 | 7980 | 7.5188 | 51600 | 9500 | 5.4316 | 6.41 | Split_Floor_Standing York 5TR SEER 6.41 | Split_Floor_Standing LG 4.5TR SEER 10.00
896 | Split_Wall_Mounted | Mando | YE3SD30RSHYW22 / YE3HW30SH7AC22 | Non-Inverter | 2.5 | 2.5 | 30000 | 3990 | 7.5188 | 25800 | 4750 | 5.4316 | 6.41 | Split_Wall_Mounted Mando 2.5TR SEER 6.41 | Split_Wall_Mounted Royal Temp 2.5TR SEER 7.53
897 | Split_Floor_Standing | York | MFTGA50CRN / MFTGA50CRN | Non-Inverter | 4 | 3.86 | 46403 | 3824 | 12.1347 | 41381 | 4794 | 8.6318 | 10.32 | Split_Floor_Standing York 3.86TR SEER 10.32 | Split_Floor_Standing LG 3.75TR SEER 7.47
898 | Split_Wall_Mounted | York | YE3SD240SHZW22 / YE3HW24SH7BC22 | Non-Inverter | 2 | 2 | 24000 | 3190 | 7.5235 | 20640 | 3820 | 5.4031 | 6.4 | Split_Wall_Mounted York 2TR SEER 6.4 | Split_Wall_Mounted Zamil 2TR SEER 6.69
899 | Split_Wall_Mounted | York | YE3SD24RSHZW22 / YE3HC24SH3BC22 | Non-Inverter | 2 | 2 | 24000 | 3190 | 7.5235 | 20640 | 3820 | 5.4031 | 6.4 | Split_Wall_Mounted York 2TR SEER 6.4 | Split_Wall_Mounted Zamil 1.83TR SEER 7.51
900 | Split_Wall_Mounted | York | YE3SD30RSHYW22-I / YE3HC30SH7AC22 | Non-Inverter | 2.5 | 2.5 | 30000 | 3990 | 7.5188 | 25800 | 4750 | 5.4316 | 6.41 | Split_Wall_Mounted York 2.5TR SEER 6.41 | Split_Wall_Mounted Royal Temp 2.5TR SEER 7.53
901 | Split_Wall_Mounted | LG | YE3SD240SHZW22 / YE3HC24SH7BC22 | Non-Inverter | 2 | 2 | 24000 | 3100 | 7.7419 | 20640 | 3820 | 5.4031 | 6.54 | Split_Wall_Mounted LG 2TR SEER 6.54 | Split_Wall_Mounted Zamil 2TR SEER 6.69
902 | Split_Wall_Mounted | Bancool | YE3SD30RSHYW22 / YE3HW30SH7AB22 | Non-Inverter | 2.5 | 2.5 | 30000 | 3990 | 7.5188 | 25800 | 4750 | 5.4316 | 6.41 | Split_Wall_Mounted Bancool 2.5TR SEER 6.41 | Split_Wall_Mounted Royal Temp 2.5TR SEER 7.53
903 | Split_Wall_Mounted | LG | S24A2MR | Non-Inverter | 2 | 2 | 24000 | 3050 | 7.8689 |  |  |  |  | Split_Wall_Mounted LG 2TR SEER | Split_Wall_Mounted DAEWOO 2TR SEER 7.86
904 | Split_Wall_Mounted | York | YE3CF18SH7BC22 | Non-Inverter | 1.5 | 1.5 | 18000 | 2390 | 7.5314 |  |  |  |  | Split_Wall_Mounted York 1.5TR SEER | Split_Wall_Mounted LG 1.46TR SEER 7.56
905 | Split_Wall_Mounted | General | AD1GH24SA2 | Non-Inverter | 1.5 | 1.56 | 18835.0238 | 2500 | 7.534 |  |  |  |  | Split_Wall_Mounted General 1.56TR SEER | Split_Wall_Mounted LG 1.46TR SEER 7.56
906 | Split_Wall_Mounted | LG | LS-H322MMB0 | Non-Inverter | 2.5 | 2.66 | 32000 | 4200 | 7.619 |  |  |  |  | Split_Wall_Mounted LG 2.66TR SEER | Split_Wall_Mounted Royal Temp 2.5TR SEER 7.53
907 | Split_Wall_Mounted | York | YTHA28OSAADA | Non-Inverter | 2 | 2.29 | 27500 | 3354 | 8.1992 |  |  |  |  | Split_Wall_Mounted York 2.29TR SEER | Split_Wall_Mounted LG 2.21TR SEER 8.14
908 | Split_Wall_Mounted | York | YE3HC18SH7BC22 | Non-Inverter | 1.5 | 1.5 | 18000 | 2390 | 7.5314 | 15480 | 2850 | 5.4316 | 6.42 | Split_Wall_Mounted York 1.5TR SEER 6.42 | Split_Wall_Mounted LG 1.41TR SEER 6.94
909 | Split_Wall_Mounted | Classic | KXC18CSIHIQ - ADX18EHAXFQ | Non-Inverter | 1.5 | 1.49 | 17995 | 2250 | 7.9978 | 14996 | 2500 | 5.9984 | 6.87 | Split_Wall_Mounted Classic 1.49TR SEER 6.87 | Split_Wall_Mounted LG 1.41TR SEER 6.94
910 | Split_Wall_Mounted | LG | S3624HUV0 | Non-Inverter | 2.5 | 2.66 | 32005 | 3850 | 8.313 | 28012 | 4600 | 6.0896 | 7.12 | Split_Wall_Mounted LG 2.66TR SEER 7.12 | Split_Wall_Mounted Royal Temp 2.67TR SEER 7.44
911 | Split_Wall_Mounted | York | YE3SD30RSHYW22-1 | Non-Inverter | 2.5 | 2.5 | 30000 | 3990 | 7.5188 | 25800 | 4750 | 5.4316 | 6.41 | Split_Wall_Mounted York 2.5TR SEER 6.41 | Split_Wall_Mounted Royal Temp 2.5TR SEER 7.53
912 | Split_Wall_Mounted | Classic | HWX36EHAYGQ | Non-Inverter | 3 | 2.79 | 33489 | 4100 | 8.168 | 27992 | 4560 | 6.1386 | 7.02 | Split_Wall_Mounted Classic 2.79TR SEER 7.02 | Split_Wall_Mounted Carrier 2.75TR SEER 8.81
913 | Split_Wall_Mounted | LG | S3624HNV0 | Non-Inverter | 2.5 | 2.66 | 32005 | 3850 | 8.313 | 28013 | 4600 | 6.0898 | 7.12 | Split_Wall_Mounted LG 2.66TR SEER 7.12 | Split_Wall_Mounted Royal Temp 2.67TR SEER 7.44
914 | Split_Wall_Mounted | Classic | KXC36CSIHAQ | Non-Inverter | 3 | 2.79 | 33490 | 4100 | 8.1683 | 27993 | 4560 | 6.1388 | 7.02 | Split_Wall_Mounted Classic 2.79TR SEER 7.02 | Split_Wall_Mounted LG 2.6TR SEER 7.18
915 | Split_Wall_Mounted | Queen | HQSGO 18H | Non-Inverter | 1.5 | 1.5 | 18083 | 2220 | 8.1455 | 15695 | 2700 | 5.813 | 6.92 | Split_Wall_Mounted Queen 1.5TR SEER 6.92 | Split_Wall_Mounted LG 1.41TR SEER 6.94
916 | Split_Wall_Mounted | Speed_Cool | UTS18LSHR | Non-Inverter | 1.5 | 1.5 | 18000 | 2250 | 8 |  |  |  |  | Split_Wall_Mounted Speed_Cool 1.5TR SEER | Split_Wall_Mounted LG 1.54TR SEER 8.14
917 | Split_Wall_Mounted | LG | NF242C3NK0 | Inverter | 2 | 1.79 | 21500 | 1734 | 12.3991 | 18500 | 2127 | 8.6977 | Inverter | Split_Wall_Mounted LG 1.79TR SEER Inverter | Inverter unit "No replacement"
918 | Split_Wall_Mounted | LG | NS182C2NK0 | Inverter | 1.5 | 1.5 | 18000 | 1452 | 12.3967 | 15300 | 1759 | 8.6981 | Inverter | Split_Wall_Mounted LG 1.5TR SEER Inverter | Inverter unit "No replacement"
919 | Split_Wall_Mounted | LG | NS242H3NK0 | Inverter | 2 | 1.79 | 21500 | 1734 | 12.3991 | 18500 | 2127 | 8.6977 | Inverter | Split_Wall_Mounted LG 1.79TR SEER Inverter | Inverter unit "No replacement"
920 | Split_Wall_Mounted | LG | NS182C2 | Inverter | 1.5 | 1.5 | 18000 | 1452 | 12.3967 | 15300 | 1759 | 8.6981 | Inverter | Split_Wall_Mounted LG 1.5TR SEER Inverter | Inverter unit "No replacement"
921 | Split_Wall_Mounted | Panasonic | CS-YW24WKS | Inverter | 2 | 1.75 | 21000 | 1721 | 12.2022 | 19200 | 2207 | 8.6996 | Inverter | Split_Wall_Mounted Panasonic 1.75TR SEER Inverter | Inverter unit "No replacement"
922 | Split_Wall_Mounted | Zamil | MRZ24CDGHIAD1 | Inverter | 2 | 1.83 | 22000 | 1781 | 12.3526 | 18434.188 | 2114 | 8.7201 | Inverter | Split_Wall_Mounted Zamil 1.83TR SEER Inverter | Inverter unit "No replacement"
923 | Split_Wall_Mounted | Samsung | AR24JQFNCWKN | Inverter | 1.5 | 1.66 | 20000 | 1630 | 12.2699 | 16500 | 1930 | 8.5492 | Inverter | Split_Wall_Mounted Samsung 1.66TR SEER Inverter | Inverter unit "No replacement"
924 | Split_Wall_Mounted | Samsung | AR30JSFUCWKN | Inverter | 2 | 2.2 | 26500 | 2300 | 11.5217 | 22000 | 2650 | 8.3019 | Inverter | Split_Wall_Mounted Samsung 2.2TR SEER Inverter | Inverter unit "No replacement"
925 | Split_Wall_Mounted | LG | NS182C2UK0 | Inverter | 1.5 | 1.5 | 18000 | 1452 | 12.3967 | 15300 | 1759 | 8.6981 | Inverter | Split_Wall_Mounted LG 1.5TR SEER Inverter | Inverter unit "No replacement"
926 | Split_Wall_Mounted | Zamil | MAZ24CHXAD1 | Non-Inverter | 2 | 1.83 | 22000 | 1781 | 12.3526 | 18434.188 | 2114 | 8.7201 | 10.44 | Split_Wall_Mounted Zamil 1.83TR SEER 10.44 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
927 | Split_Floor_Standing | Kelvinator | KIQ060SHAA | Non-Inverter | 5 | 5 | 60000 | 7980 | 7.5188 | 51600 | 9500 | 5.4316 | 6.41 | Split_Floor_Standing Kelvinator 5TR SEER 6.41 | Split_Floor_Standing LG 4.5TR SEER 10.00
928 | Split_Floor_Standing | LG | LP-K3023HL | Non-Inverter | 2 | 2.3 | 27638.3502 | 3420 | 8.0814 | 21837.7088 | 3730 | 5.8546 | 6.85 | Split_Floor_Standing LG 2.3TR SEER 6.85 | No Equivalent Found provide Pic & Datasheets
929 | Split_Floor_Standing | York | YE3SD60SECAA22 / YE3FS60SC7AA22 | Non-Inverter | 5 | 5 | 60000 | 7980 | 7.5188 | 51600 | 9500 | 5.4316 | 6.41 | Split_Floor_Standing York 5TR SEER 6.41 | Split_Floor_Standing LG 4.5TR SEER 10.00
930 | Split_Wall_Mounted | York | YE5SD240SHZW22 / YE5HC24SH7BC22 | Non-Inverter | 2 | 1.87 | 22500 | 2361 | 9.5299 | 19870 | 2863 | 6.9403 | 8.15 | Split_Wall_Mounted York 1.87TR SEER 8.15 | Split_Wall_Mounted LG 1.74TR SEER 8.17
931 | Split_Wall_Mounted | Midea | SHDC24ON-GDE / SHEC24ON-BDE | Non-Inverter | 2 | 1.91 | 23000 | 1870 | 12.2995 | 19800 | 2275 | 8.7033 | 10.42 | Split_Wall_Mounted Midea 1.91TR SEER 10.42 | Split_Wall_Mounted Zamil 1.83TR SEER 10.42
932 | Split_Wall_Mounted | LG | LP-K3023CL | Non-Inverter | 2.5 | 2.5 | 30000 | 3400 | 8.8235 |  |  |  |  | Split_Wall_Mounted LG 2.5TR SEER | Split_Wall_Mounted Carrier 2.75TR SEER 8.81
933 | Split_Floor_Standing | LG | LP-5091NC | Non-Inverter | 4 | 4.16 | 50000 | 6000 | 8.3333 |  |  |  |  | Split_Floor_Standing LG 4.16TR SEER | Split_Floor_Standing LG 4.49TR SEER 8.28
934 | Split_Floor_Standing | Mitsubishi | PUH-6TKSA | Non-Inverter | 5 | 5 | 60000 | 5870 | 10.2215 |  |  |  |  | Split_Floor_Standing Mitsubishi 5TR SEER | Split_Floor_Standing LG 4.5TR SEER 10.00
935 | Split_Floor_Standing | GoldStar | LP-5090NH | Non-Inverter | 4 | 4.16 | 50000 | 6000 | 8.3333 |  |  |  |  | Split_Floor_Standing GoldStar 4.16TR SEER | Split_Floor_Standing LG 4.49TR SEER 8.28
936 | Split_Floor_Standing | LAKES | LFAC-50H/A | Non-Inverter | 4 | 4.16 | 50000 | 5990 | 8.3472 |  |  |  |  | Split_Floor_Standing LAKES 4.16TR SEER | Split_Floor_Standing LG 4.49TR SEER 8.28
937 | Split_Wall_Mounted | York | YE8CF24SC7AC41 | Non-Inverter | 2 | 2 | 24000 | 2000 | 12 | 21400 | 2503 | 8.5497 | 10.21 | Split_Wall_Mounted York 2TR SEER 10.21 | Split_Wall_Mounted Gree 1.83TR SEER 10.17
938 | Split_Wall_Mounted | LG | LVNC242BLA0 | Non-Inverter | 2 | 2 | 24100 | 2600 | 9.2692 |  |  |  |  | Split_Wall_Mounted LG 2TR SEER | Split_Wall_Mounted Zamil 1.99TR SEER9.77
939 | Split_Wall_Mounted | Samsung | FC24BTVA | Non-Inverter | 2 | 1.91 | 23000 | 2700 | 8.5185 |  |  |  |  | Split_Wall_Mounted Samsung 1.91TR SEER | Split_Wall_Mounted Carrier 2TR SEER 8.60
940 | Split_Wall_Mounted | Trane | 4MXDUA18T1000AA | Non-Inverter | 1.5 | 1.48 | 17800 | 1480 | 12.027 | 16000 | 1850 | 8.6486 | 10.27 | Split_Wall_Mounted Trane 1.48TR SEER 10.27 | Split_Wall_Mounted Cooline 1.5TR SEER 10.25
941 | Split_Floor_Standing | Samsung | AF55JV1MAEEN | Inverter | 4 | 4 | 48000 | 3930 | 12.2137 | 42000 | 4950 | 8.4848 | Inverter | Split_Floor_Standing Samsung 4TR SEER Inverter | Inverter unit "No replacement"
942 | Split_Ceiling_Ducted | York | YE3Cf24CS7AC22 | Non-Inverter | 2 | 2 | 24000 | 3190 | 7.5235 | 20640 | 3800 | 5.4316 | 6.41 | Split_Ceiling_Ducted York 2TR SEER 6.41 | Split_Ceiling_Ducted YORK 2TR SEER 6.41
943 | Split_Ceiling_Cassette | Goodman | ECM24SHAC | Non-Inverter | 2 | 2 | 24000 | 3190 | 7.5235 | 20640 | 3800 | 5.4316 | 6.41 | Split_Ceiling_Cassette Goodman 2TR SEER 6.41 | Split_Ceiling_Cassette Mitsubishi 2.02TR SEER 6.93
944 | Window | Hyundai | HYWAC1810C | Non-Inverter | 1.5 | 1.48 | 17844.76 | 2180 | 8.18 | 0 | 0 |  | - | Window Hyundai 1.48TR SEER - | Window LG 1.5TR SEER 7.70
945 | Window | Horizon | WR184HBPA | Non-Inverter | 1.5 | 1.5 | 18000 | 2500 | 7.2 | 0 | 0 |  | - | Window Horizon 1.5TR SEER - | Window LG 1.5TR SEER 7.70
946 | Window | General | ARM18KEM2 | Non-Inverter | 1.5 | 1.5 | 18000 | 0 |  | 0 | 0 |  | - | Window General 1.5TR SEER - | Window LG 1.5TR SEER 7.70
947 | Window | Zamil | LCB19CTXCIING | Non-Inverter | 1.5 | 1.58 | 19000 | 2150 | 8.83 | 13750 | 2350 | 5.8511 | 7.26 | Window Zamil 1.58TR SEER 7.26 | Window LG 1.49TR SEER 7.24
948 | Window | Coolsense | AMJCSP24WAC | Non-Inverter | 1.5 | 1.7 | 20500 | 1990.2913 | 10.3 | 0 | 0 |  | - | Window Coolsense 1.7TR SEER - | Window York 1.75TR SEER 8.45
949 | Window | General Electric | ARM18KAJ | Non-Inverter | 1.5 | 1.5 | 18000 | 2900 | 6.2 | 0 | 0 |  | - | Window General Electric 1.5TR SEER - | Window Zamil 1.5TR SEER 6.51
950 | Window | Toshiba | RAC-18LE2B | Non-Inverter | 1.5 | 1.5 | 18000 | 0 |  | 0 | 0 |  | - | Window Toshiba 1.5TR SEER - | Window LG 1.5TR SEER 7.70
951 | Window | Carrier | 51GVD218-3 | Non-Inverter | 1.5 | 1.5 | 18000 | 2450 | 7.34 | 14193.92 | 2750 | 5.1614 | 6.98 | Window Carrier 1.5TR SEER 6.98 | Window Zamil 1.5TR SEER 6.51
952 | Window | Alessa | CO19E8Y1 | Non-Inverter | 1.5 | 1.54 | 18500 | 2320 | 7.97 | 0 | 0 |  | - | Window Alessa 1.54TR SEER - | Window LG 1.5TR SEER 7.70
953 | Window | Amana | 624-3HW | Non-Inverter | 2 | 1.91 | 23000 | 3565 | 6.45 | 0 | 0 |  | - | Window Amana 1.91TR SEER - | Window Royal Temp 2TR SEER 6.41
954 | Window | Craft | O19E8JI | Non-Inverter | 1.5 | 1.54 | 18500 | 2450 | 7.55 | 0 | 0 |  | - | Window Craft 1.54TR SEER - | Window LG 1.5TR SEER 7.70
955 | Window | Craft | AO19E8A2 | Non-Inverter | 1.5 | 1.5 | 18000 | 2480 | 7.25 | 0 | 0 |  | - | Window Craft 1.5TR SEER - | Window LG 1.5TR SEER 7.70
956 | Window | Craft | O19E8H4 | Non-Inverter | 1.5 | 1.47 | 17742.4 | 1948 | 9.1 | 0 | 0 |  | - | Window Craft 1.47TR SEER - | Window Carrier 1.5TR SEER 8.62
957 | Window | Falcon | NECH19L | Non-Inverter | 1.5 | 1.55 | 18600 | 2450 | 7.59 | 0 | 0 |  | - | Window Falcon 1.55TR SEER - | Window LG 1.5TR SEER 7.70
958 | Window | Falcon | FSE24 | Non-Inverter | 2 | 2 | 24000 | 2970 | 8.08 | 0 | 0 |  | - | Window Falcon 2TR SEER - | Window LG 2TR SEER 7.48
959 | Window | Falcon | NFCH19L | Non-Inverter | 1.5 | 1.55 | 18600 | 2450 | 7.59 | 0 | 0 |  | - | Window Falcon 1.55TR SEER - | Window LG 1.5TR SEER 7.70
960 | Window | Friedrich | NH230 | Non-Inverter | 2 | 1.91 | 23000 | 3300 | 6.96 | 0 | 0 |  | - | Window Friedrich 1.91TR SEER - | Window LG 2TR SEER 7.48
961 | Window | General | AXS-S | Non-Inverter | 2 | 1.8 | 21600 | 2429.6963 | 8.89 | 18300 | 2900.1585 | 6.31 | 7.53 | Window General 1.8TR SEER 7.53 | Window Zamil 1.88TR SEER 7.28
962 | Window | General | ARJ24BDS1 | Non-Inverter | 2 | 1.84 | 22092.7 | 2890 | 7.64 | 0 | 0 |  | - | Window General 1.84TR SEER - | Window LG 2TR SEER 7.48
963 | Window | General | EWAH 19K5-W | Non-Inverter | 1.5 | 1.55 | 18600 | 2450 | 7.59 | 0 | 0 |  | - | Window General 1.55TR SEER - | Window Zamil 1.5TR SEER 6.51
964 | Window | General_Supreme | GS183AH | Non-Inverter | 1.5 | 1.48 | 17800 | 2057.8035 | 8.65 | 0 | 0 |  | - | Window General_Supreme 1.48TR SEER - | Window Carrier 1.5TR SEER 8.62
965 | Window | GIBSON | AK18E8NHBB-25kW | Non-Inverter | 1.5 | 1.5 | 18000 | 3000 | 6 | 0 | 0 |  | - | Window GIBSON 1.5TR SEER - | Window Zamil 1.5TR SEER 6.51
966 | Window | Gree | GJE18AG-D1MTD5E | Non-Inverter | 1.5 | 1.41 | 17000 | 1830 | 9.28 | 14600 | 2200 | 6.6364 | 7.89 | Window Gree 1.41TR SEER 7.89 | Window LG 1.5TR SEER 7.70
967 | Window | Kelvinator | KSVR243M-OM | Non-Inverter | 2 | 2 | 24000 | 2700 | 8.88 | 0 | 0 |  | - | Window Kelvinator 2TR SEER - | Window LG 2TR SEER 7.48
968 | Window | Kelvinator | SAKH19 | Non-Inverter | 1.5 | 1.54 | 18563 | 0 |  | 0 | 0 |  | - | Window Kelvinator 1.54TR SEER - | Window LG 1.5TR SEER 7.70
969 | Window | Kelvinator | KSVD243M-1C | Non-Inverter | 2 | 2 | 24000 | 2600 | 9.23 | 24000 | 2800 | 8.5714 | - | Window Kelvinator 2TR SEER - | Window LG 2TR SEER 7.48
970 | Window | Kelvinator | KSVD183M-0K | Non-Inverter | 1.5 | 1.5 | 18000 | 2200 | 8.18 | 15000 | 2500 | 6 | 6.98 | Window Kelvinator 1.5TR SEER 6.98 | Window LG 1.39TR SEER 7.03
971 | Window | Kelvinator | KSVR183M-OM | Non-Inverter | 1.5 | 1.5 | 18000 | 0 |  | 0 | 0 |  | - | Window Kelvinator 1.5TR SEER - | Window LG 1.5TR SEER 7.70
972 | Window | LG | E182BR | Non-Inverter | 1.5 | 1.48 | 17878.88 | 1820 | 9.82 | 15354 | 2170 | 7.0756 | 8.36 | Window LG 1.48TR SEER 8.36 | Window Carrier 1.43TR SEER 8.52
973 | Window | LG | LWH242MFAB1 | Non-Inverter | 2 | 2 | 24000 | 2560 | 9.37 | 0 | 0 |  | - | Window LG 2TR SEER - | Window LG 2TR SEER 7.48
974 | Window | MESTCOOL | MZVR183M-OS3 | Non-Inverter | 1.5 | 1.5 | 18000 | 2068.9655 | 8.7 | 0 | 0 |  | - | Window MESTCOOL 1.5TR SEER - | Window Carrier 1.5TR SEER 8.62
975 | Window | ALESSA | DO19EBJ | Non-Inverter | 1.5 | 1.5 | 18000 | 2375 | 7.57 | 0 | 0 |  | - | Window ALESSA 1.5TR SEER - | Window LG 1.5TR SEER 7.70
976 | Window | Other | AO18E8NHBC | Non-Inverter | 1.5 | 1.5 | 18000 | 0 |  | 0 | 0 |  | - | Window Other 1.5TR SEER - | Window LG 1.5TR SEER 7.70
977 | Window | QUEEN | HQ19HC | Non-Inverter | 1.5 | 1.55 | 18600 | 2450 | 7.59 | 0 | 0 |  | - | Window QUEEN 1.55TR SEER - | Window LG 1.5TR SEER 7.70
978 | Window | Sharp | AF-180H7MC | Non-Inverter | 1.5 | 1.5 | 18000 | 2080 | 8.65 | 0 | 0 |  | - | Window Sharp 1.5TR SEER - | Window Carrier 1.5TR SEER 8.62
979 | Window | Shogun | SHWH18M2H | Non-Inverter | 1.5 | 1.5 | 18000 | 2250 | 8 | 0 | 0 |  | - | Window Shogun 1.5TR SEER - | Window LG 1.5TR SEER 7.70
980 | Window | Starway | WAC18KHCN | Non-Inverter | 1.5 | 1.46 | 17600 | 0 |  | 0 | 0 |  | - | Window Starway 1.46TR SEER - | Window LG 1.5TR SEER 7.70
981 | Window | York | 6AY-19 | Non-Inverter | 1.5 | 1.54 | 18563 | 0 |  | 0 | 0 |  | - | Window York 1.54TR SEER - | Window LG 1.5TR SEER 7.70
982 | Window | York | SAYH19 | Non-Inverter | 1.5 | 1.54 | 18563 | 0 |  | 0 | 0 |  | - | Window York 1.54TR SEER - | Window LG 1.5TR SEER 7.70
983 | Window | Zamil | KOT18PECA | Non-Inverter | 1.5 | 1.5 | 18000 | 2390 | 7.53 | 15480 | 2850 | 5.4316 | 6.41 | Window Zamil 1.5TR SEER 6.41 | Window Zamil 1.5TR SEER 6.51
984 | Window | Ugine | UGNW18E | Non-Inverter | 1.5 | 1.5 | 18000 | 0 |  | 0 | 0 |  |  | Window Ugine 1.5TR SEER | Window LG 1.5TR SEER 7.70
985 | Split_Wall_Mounted | Kelvinator | HBPUDC24 | Non-Inverter | 2 | 2 | 24000 | 3190 | 7.52 | 20640 | 3801.105 | 5.43 | 6.4 | Split_Wall_Mounted Kelvinator 2TR SEER 6.4 | Split_Wall_Mounted Zamil 2TR SEER 6.69
986 | Split_Wall_Mounted | General Electric | AA1MH | Non-Inverter | 2 | 2.16 | 25992 | 0 |  | 0 | 0 |  |  | Split_Wall_Mounted General Electric 2.16TR SEER | Split_Wall_Mounted Zamil 2.12TR SEER 8.09
987 | Split_Wall_Mounted | omnia | AC-2450H | Non-Inverter | 2 | 2 | 24000 | 2785 | 8.61 | 0 | 0 |  |  | Split_Wall_Mounted omnia 2TR SEER | Split_Wall_Mounted Carrier 2TR SEER 8.60
988 | Split_Wall_Mounted | flix | AO-S-FLX-2400-H | Non-Inverter | 1.5 | 1.62 | 19550 | 1700 | 11.5 | 17264 | 2080 | 8.3 | 9.81 | Split_Wall_Mounted flix 1.62TR SEER 9.81 | Split_Wall_Mounted Zamil 1.47TR SEER 9.8
989 | Split_Wall_Mounted | Zamil | ADL18EHAXIW | Non-Inverter | 1.5 | 1.5 | 18000 | 0 |  | 0 | 0 |  |  | Split_Wall_Mounted Zamil 1.5TR SEER | Split_Wall_Mounted GREE 1.5TR SEER 9.98
990 | Split_Wall_Mounted | Zamil | ADL24EHAXIW | Non-Inverter | 2 | 2 | 24000 | 0 |  | 0 | 0 |  |  | Split_Wall_Mounted Zamil 2TR SEER | Split_Wall_Mounted Zamil 2TR SEER 10.39
991 | Split_Wall_Mounted | Zamil | ADX18EHAXI | Non-Inverter | 2 | 2 | 24000 | 0 |  | 0 | 0 |  |  | Split_Wall_Mounted Zamil 2TR SEER | Split_Wall_Mounted Zamil 2TR SEER 10.39
992 | Split_Wall_Mounted | sharp | AH-A18WCS | Non-Inverter | 1.5 | 1.5 | 18000 | 1481 | 12.15 | 15000 | 1754.386 | 8.55 | 10.25 | Split_Wall_Mounted sharp 1.5TR SEER 10.25 | Split_Wall_Mounted Cooline 1.5TR SEER 10.25
993 | Split_Wall_Mounted | Samsung | AR18KRFHCWKNMG | Non-Inverter | 1.5 | 1.43 | 17200 | 1480 | 11.62 | 15000 | 1775.1479 | 8.45 | 9.92 | Split_Wall_Mounted Samsung 1.43TR SEER 9.92 | Split_Wall_Mounted Chigo 1.38TR SEER 9.88
994 | Split_Wall_Mounted | Aukia | ASTW-24B2/KDA | Non-Inverter | 2 | 1.91 | 22996.88 | 2460 | 9.34 | 19994.32 | 3038.6505 | 6.58 | 7.91 | Split_Wall_Mounted Aukia 1.91TR SEER 7.91 | Split_Wall_Mounted Carrier 1.81TR SEER 7.91
995 | Split_Wall_Mounted | Aukia | Aukp24cc | Non-Inverter | 2 | 1.84 | 22178 | 1820 | 12.18 | 19107 | 2196.2069 | 8.7 | 10.34 | Split_Wall_Mounted Aukia 1.84TR SEER 10.34 | Split_Wall_Mounted Crown 1.79TR SEER 10.33
996 | Split_Wall_Mounted | AUX | AUX18CDC | Non-Inverter | 1.5 | 1.53 | 18400 | 1610 | 11.42 | 15422.24 | 1800 | 8.5679 | 9.81 | Split_Wall_Mounted AUX 1.53TR SEER 9.81 | Split_Wall_Mounted LG 1.46TR SEER 9.8
997 | Split_Wall_Mounted | LG | B2428H | Non-Inverter | 1.5 | 1.74 | 20949.68 | 1820 | 11.51 | 18936.6 | 2278.7726 | 8.31 | 9.84 | Split_Wall_Mounted LG 1.74TR SEER 9.84 | Split_Wall_Mounted LG 1.74TR SEER 9.84
998 | Split_Wall_Mounted | Coolex | CCO-030 | Non-Inverter | 2 | 2.01 | 24194 | 2043 | 11.84 | 20847 | 2467.1006 | 8.45 | 10.05 | Split_Wall_Mounted Coolex 2.01TR SEER 10.05 | Split_Wall_Mounted GREE 2.19TR SEER 10.05
999 | Split_Wall_Mounted | Champion | CHSL180C | Non-Inverter | 1.5 | 1.53 | 18400 | 1510 | 12.18 | 15800 | 1795.4545 | 8.8 | 10.37 | Split_Wall_Mounted Champion 1.53TR SEER 10.37 | Split_Wall_Mounted Okia 1.53TR SEER 10.37
1000 | Split_Wall_Mounted | Champion | CHSS-12H | Non-Inverter | 1 | 0.89 | 10747.8 | 1250 | 8.59 | 8250.216 | 1374 | 6.0045 | 7.2 | Split_Wall_Mounted Champion 0.89TR SEER 7.2 | Split_Wall_Mounted LG 0.95TR SEER 7.9
1001 | Split_Wall_Mounted | Blue power | CSA-24CH | Non-Inverter | 1.5 | 1.73 | 20813.2 | 2320 | 8.97 | 17742.4 | 2656.0479 | 6.68 | 7.7 | Split_Wall_Mounted Blue power 1.73TR SEER 7.7 | Split_Wall_Mounted Carrier 1.75TR SEER 7.63
1002 | Split_Wall_Mounted | Panasonic | CS-YV18TKS | Non-Inverter | 1.5 | 1.47 | 17742 | 1504 | 11.79 | 15886 | 1868.9412 | 8.5 | 10.07 | Split_Wall_Mounted Panasonic 1.47TR SEER 10.07 | Split_Wall_Mounted LG 1.47TR SEER 10.15
1003 | Split_Wall_Mounted | Craft | DSA25CE7GR7N | Non-Inverter | 1.5 | 1.79 | 21500 | 1822 | 11.8 | 17700 | 2082.3529 | 8.5 | 10.01 | Split_Wall_Mounted Craft 1.79TR SEER 10.01 | Split_Wall_Mounted Carrier 1.83TR SEER 10.08
1004 | Split_Wall_Mounted | Craft | DSW24FE7HY7M | Non-Inverter | 2 | 1.83 | 22000 | 1870 | 11.76 | 19400 | 2250 | 8.6222 | 10.08 | Split_Wall_Mounted Craft 1.83TR SEER 10.08 | Split_Wall_Mounted Carrier 1.83TR SEER 10.08
1005 | Split_Wall_Mounted | dansat | dac-18wch | Non-Inverter | 1.5 | 1.49 | 17913 | 1450 | 12.35 | 15350 | 1760 | 8.7216 | 10.45 | Split_Wall_Mounted dansat 1.49TR SEER 10.45 | Split_Wall_Mounted LG 1.5TR SEER 10.46
1006 | Split_Wall_Mounted | Craft | DS18FE7SCWT | Non-Inverter | 1.5 | 1.5 | 18000 | 1475 | 12.2 | 15500 | 1823 | 8.5025 | 10.29 | Split_Wall_Mounted Craft 1.5TR SEER 10.29 | Split_Wall_Mounted Cooline 1.5TR SEER 10.25
1007 | Split_Wall_Mounted | Craft | DSA120FE7H | Non-Inverter | 1.5 | 1.5 | 18000 | 1450 | 12.41 | 15300 | 1758.6207 | 8.7 | 10.47 | Split_Wall_Mounted Craft 1.5TR SEER 10.47 | Split_Wall_Mounted LG 1.5TR SEER 10.46
1008 | Split_Wall_Mounted | Craft | DSA125FE7H | Non-Inverter | 2 | 1.83 | 22000 | 1775 | 12.39 | 19000 | 2196.5318 | 8.65 | 10.46 | Split_Wall_Mounted Craft 1.83TR SEER 10.46 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
1009 | Split_Wall_Mounted | Craft | DSA24FE7YHA1 | Non-Inverter | 2 | 1.91 | 23000 | 1855 | 12.39 | 19800 | 2275 | 8.7033 | 10.48 | Split_Wall_Mounted Craft 1.91TR SEER 10.48 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
1010 | Split_Wall_Mounted | Kelvinator | Eza18sh/GQR183MIO-M0 | Non-Inverter | 1.5 | 1.5 | 18000 | 2390 | 7.53 | 15480 | 2850 | 5.4316 | 6.41 | Split_Wall_Mounted Kelvinator 1.5TR SEER 6.41 | Split_Wall_Mounted LG 1.41TR SEER 6.94
1011 | Split_Wall_Mounted | Galanz | GACSH-18H | Non-Inverter | 1.5 | 1.5 | 18000 | 2040 | 8.82 | 8530 | 1343.3071 | 6.35 | 7.22 | Split_Wall_Mounted Galanz 1.5TR SEER 7.22 | Split_Wall_Mounted LG 1.46TR SEER 7.28
1012 | Split_Wall_Mounted | General | GENP24HRS | Non-Inverter | 2 | 1.83 | 22000 | 1800 | 12.22 | 18800 | 2200 | 8.5455 | 10.31 | Split_Wall_Mounted General 1.83TR SEER 10.31 | Split_Wall_Mounted Crown 1.79TR SEER 10.33
1013 | Split_Wall_Mounted | Kelvinator | KIZB18SH | Non-Inverter | 1.5 | 1.42 | 17040 | 1500 | 11.36 | 15097 | 1818.9157 | 8.3 | 9.73 | Split_Wall_Mounted Kelvinator 1.42TR SEER 9.73 | Split_Wall_Mounted LG 1.46TR SEER 9.8
1014 | Split_Wall_Mounted | Kelvinator | HBPUDC18 | Non-Inverter | 1.5 | 1.5 | 18000 | 2390 | 7.53 | 15480 | 2850.8287 | 5.43 | 6.41 | Split_Wall_Mounted Kelvinator 1.5TR SEER 6.41 | Split_Wall_Mounted LG 1.41TR SEER 6.94
1015 | Split_Wall_Mounted | Queen | Hqit24h | Non-Inverter | 1.5 | 1.71 | 20523.18 | 2550 | 8.04 | 0 | 0 |  |  | Split_Wall_Mounted Queen 1.71TR SEER | Split_Wall_Mounted LG 1.54TR SEER 8.14
1016 | Split_Wall_Mounted | Queen | HQSMI24H | Non-Inverter | 1.5 | 1.79 | 21495.6 | 3500 | 6.14 | 0 | 0 |  |  | Split_Wall_Mounted Queen 1.79TR SEER | Split_Wall_Mounted Zamil 2TR SEER 6.69
1017 | Split_Wall_Mounted | Queen | HQSMI30H | Non-Inverter | 2 | 1.83 | 22007.4 | 3700 | 5.94 | 0 | 0 |  |  | Split_Wall_Mounted Queen 1.83TR SEER | Split_Wall_Mounted Zamil 2TR SEER 6.69
1018 | Split_Wall_Mounted | Haas | HSA12FE7HH7 | Non-Inverter | 1 | 1 | 12000 | 985 | 12.18 | 10500 | 1160 | 9.0517 | 10.47 | Split_Wall_Mounted Haas 1TR SEER 10.47 | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
1019 | Split_Wall_Mounted | Haas | Hsa18fe7hg | Non-Inverter | 1.5 | 1.5 | 18000 | 0 |  | 0 | 0 |  |  | Split_Wall_Mounted Haas 1.5TR SEER | Split_Wall_Mounted GREE 1.5TR SEER 9.98
1020 | Split_Wall_Mounted | Kelvinator | Hscu24hb | Non-Inverter | 2 | 2 | 24000 | 0 |  | 0 | 0 |  |  | Split_Wall_Mounted Kelvinator 2TR SEER | Split_Wall_Mounted Zamil 2TR SEER 10.39
1021 | Split_Wall_Mounted | Haier | HSU-18HEK13 | Non-Inverter | 1.5 | 1.42 | 17060 | 1680 | 10.15 | 14671.6 | 1900 | 7.7219 | 8.76 | Split_Wall_Mounted Haier 1.42TR SEER 8.76 | Split_Wall_Mounted LG 1.5TR SEER 8.40
1022 | Split_Wall_Mounted | Zamil | HWX18EHAXH | Non-Inverter | 1.5 | 1.5 | 18000 | 0 |  | 0 | 0 |  |  | Split_Wall_Mounted Zamil 1.5TR SEER | Split_Wall_Mounted GREE 1.5TR SEER 9.98
1023 | Split_Wall_Mounted | Kayannenergy | KAYANN-ENERGY-18K-H-SAGA-105 | Non-Inverter | 1.5 | 1.45 | 17400 | 1810 | 9.61 | 14300 | 1958.9041 | 7.3 | 8.26 | Split_Wall_Mounted Kayannenergy 1.45TR SEER 8.26 | Split_Wall_Mounted LG 1.53TR SEER 8.30
1024 | Split_Wall_Mounted | Mando | KFR-61GW/a. | Non-Inverter | 2 | 2 | 24000 | 2600 | 9.23 | 24500 | 2640.0862 | 9.28 | 8.68 | Split_Wall_Mounted Mando 2TR SEER 8.68 | Split_Wall_Mounted Carrier 2TR SEER 8.60
1025 | Split_Wall_Mounted | Haam | KT3FR-36GW/a | Non-Inverter | 1 | 0.9 | 10918.4 | 1200 | 9.09 | 9553.6 | 1392.6531 | 6.86 | 7.85 | Split_Wall_Mounted Haam 0.9TR SEER 7.85 | Split_Wall_Mounted LG 0.95TR SEER 7.9
1026 | Split_Wall_Mounted | TOPTEC | KT3FR-50GW/60 | Non-Inverter | 1.5 | 1.5 | 18000 | 2250 | 8 | 0 | 0 |  |  | Split_Wall_Mounted TOPTEC 1.5TR SEER | Split_Wall_Mounted LG 1.54TR SEER 8.14
1027 | Split_Wall_Mounted | Max plus | Maxksa30c | Non-Inverter | 2 | 2.18 | 26170 | 2200 | 11.89 | 0 | 0 |  |  | Split_Wall_Mounted Max plus 2.18TR SEER | Split_Wall_Mounted Gree 2.25TR SEER 11.11
1028 | Split_Wall_Mounted | Mitsubishi | Ms-18nn | Non-Inverter | 1.5 | 1.5 | 18000 | 0 |  | 0 | 0 |  |  | Split_Wall_Mounted Mitsubishi 1.5TR SEER | Split_Wall_Mounted GREE 1.5TR SEER 9.98
1029 | Split_Wall_Mounted | NIKAI | NSAC-1836 | Non-Inverter | 1.5 | 1.5 | 18000 | 2190 | 8.21 | 0 | 0 |  |  | Split_Wall_Mounted NIKAI 1.5TR SEER | Split_Wall_Mounted LG 1.52TR SEER 8.15
1030 | Split_Wall_Mounted | Rantic | OMR-18CH | Non-Inverter | 1.5 | 1.45 | 17401.2 | 1950 | 8.92 | 15354 | 2248.0234 | 6.83 | 7.73 | Split_Wall_Mounted Rantic 1.45TR SEER 7.73 | Split_Wall_Mounted Royal Temp 1.5TR SEER 7.67
1031 | Split_Wall_Mounted | GENERAL GOLDIN | ONG-1 EKC | Non-Inverter | 1.5 | 1.5 | 18015.36 | 1480 | 12.17 | 16377.6 | 1882.4828 | 8.7 | 10.38 | Split_Wall_Mounted GENERAL GOLDIN 1.5TR SEER 10.38 | Split_Wall_Mounted Mando 1.53TR SEER 10.38
1032 | Split_Wall_Mounted | Platinum | PLS30-C | Inverter | 2 | 2.26 | 27200 | 2194 | 12.39 | 23600 | 2712.6437 | 8.7 | 10.48 | Split_Wall_Mounted Platinum 2.26TR SEER 10.48 | Inverter unit "No replacement"
1033 | Split_Wall_Mounted | ROLLC | RASN12HP | Non-Inverter | 1 | 0.93 | 11259 | 1237.2527 | 9.1 | 0 | 0 |  |  | Split_Wall_Mounted ROLLC 0.93TR SEER | Split_Wall_Mounted LG 0.95TR SEER 8.3
1034 | Split_Wall_Mounted | FUJI | RSA18RAT | Non-Inverter | 1.5 | 1.52 | 18300 | 2160 | 8.47 | 15400 | 2421.3836 | 6.36 | 7.27 | Split_Wall_Mounted FUJI 1.52TR SEER 7.27 | Split_Wall_Mounted LG 1.46TR SEER 7.28
1035 | Split_Wall_Mounted | Rantic | Rtc24hn | Non-Inverter | 1.5 | 1.71 | 20545 | 1739 | 11.81 | 17577 | 2104.5259 | 8.352 | 10 | Split_Wall_Mounted Rantic 1.71TR SEER 10 | Split_Wall_Mounted Carrier 1.83TR SEER 10.08
1036 | Split_Wall_Mounted | LG | s182hq | Non-Inverter | 1.5 | 1.54 | 18500 | 1960 | 9.43 | 16787.04 | 2080 | 8.0707 | 8.43 | Split_Wall_Mounted LG 1.54TR SEER 8.43 | Split_Wall_Mounted LG 1.5TR SEER 8.40
1037 | Split_Wall_Mounted | LG | S192LH | Non-Inverter | 1.5 | 1.54 | 18500 | 1900 | 9.73 | 19000 | 2183.908 | 8.7 | 8.91 | Split_Wall_Mounted LG 1.54TR SEER 8.91 | Split_Wall_Mounted LG 1.5TR SEER 8.40
1038 | Split_Wall_Mounted | Haam | S-30H/Hr | Non-Inverter | 2 | 1.99 | 23884 | 2930 | 8.15 | 21495.6 | 3198.75 | 6.72 | 7.21 | Split_Wall_Mounted Haam 1.99TR SEER 7.21 | Split_Wall_Mounted Zamil 2.11TR SEER7.24
1039 | Split_Wall_Mounted | LG | S3824C Nvo | Non-Inverter | 2.5 | 2.7 | 32482.24 | 3820 | 8.5 | 28012.52 | 4599.757 | 6.09 | 7.23 | Split_Wall_Mounted LG 2.7TR SEER 7.23 | Split_Wall_Mounted Carrier 2.75TR SEER 8.81
1040 | Split_Wall_Mounted | LG | S382GQ S01 | Non-Inverter | 3 | 3.16 | 38000 | 3700 | 10.27 | 0 | 0 |  |  | Split_Wall_Mounted LG 3.16TR SEER | No Equivalent Found provide Pic & Datasheets
1041 | Split_Wall_Mounted | SAC | Sac18hc | Non-Inverter | 1.5 | 1.5 | 18000 | 0 |  | 0 | 0 |  |  | Split_Wall_Mounted SAC 1.5TR SEER | Split_Wall_Mounted GREE 1.5TR SEER 9.98
1042 | Split_Wall_Mounted | SREEN | SREEN24CS | Non-Inverter | 1.5 | 1.78 | 21400 | 1761 | 12.15 | 18600 | 2175.4386 | 8.55 | 10.28 | Split_Wall_Mounted SREEN 1.78TR SEER 10.28 | Split_Wall_Mounted Mando 1.84TR SEER 10.28
1043 | Split_Wall_Mounted | tcl | tac-12cs/et2 | Non-Inverter | 1 | 0.89 | 10768.272 | 1299 | 8.28 | 0 | 0 |  |  | Split_Wall_Mounted tcl 0.89TR SEER | Split_Wall_Mounted LG 0.95TR SEER 8.3
1044 | Split_Wall_Mounted | TERIM | TRG30C717 | Non-Inverter | 2 | 2.27 | 27300 | 2310 | 11.81 | 23000 | 2705 | 8.5028 | 10.04 | Split_Wall_Mounted TERIM 2.27TR SEER 10.04 | Split_Wall_Mounted GREE 2.19TR SEER 10.05
1045 | Split_Wall_Mounted | York | YE8SD240SCBC41- HB | Non-Inverter | 2 | 1.83 | 22000 | 1800 | 12.22 | 18200 | 2128.655 | 8.55 | 10.29 | Split_Wall_Mounted York 1.83TR SEER 10.29 | Split_Wall_Mounted Mando 1.84TR SEER 10.28
1046 | Split_Wall_Mounted | York | YHGE18XT2BFE-R3 | Non-Inverter | 1.5 | 1.47 | 17700 | 1480 | 11.95 | 15200 | 1760 | 8.6364 | 10.18 | Split_Wall_Mounted York 1.47TR SEER 10.18 | Split_Wall_Mounted General 1.5TR SEER 10.16
1047 | Split_Wall_Mounted | York | YHGE30XT3CFE-R4 | Non-Inverter | 2 | 2.26 | 27200 | 2210 | 12.3 | 23000 | 0 |  |  | Split_Wall_Mounted York 2.26TR SEER | Split_Wall_Mounted Gree 2.25TR SEER 11.11
1048 | Split_Wall_Mounted | Samsung | AR18TQHQCWKX | Inverter | 1.5 | 1.5 | 18000 | 1452 | 12.39 | 15900 | 1797 | 8.8481 | 10.54 | Split_Wall_Mounted Samsung 1.5TR SEER 10.54 | Inverter unit "No replacement"
1049 | Split_Wall_Mounted | Samsung | AS24EAPX | Non-Inverter | 2 | 2 | 24000 | 2750 | 8.72 | 19841 | 3200 | 6.2003 | 7.38 | Split_Wall_Mounted Samsung 2TR SEER 7.38 | Split_Wall_Mounted Zamil 1.83TR SEER 7.51
1050 | Split_Wall_Mounted | SHARP | AU-A18WCS | Non-Inverter | 1.5 | 1.5 | 18000 | 1481 | 12.15 | 15000 | 1754 | 8.5519 | 10.25 | Split_Wall_Mounted SHARP 1.5TR SEER 10.25 | Split_Wall_Mounted Cooline 1.5TR SEER 10.25
1051 | Split_Wall_Mounted | Craft | DSXSA24CE73H2 | Non-Inverter | 2 | 2 | 24000 | 2720 | 8.82 | 0 | 0 |  |  | Split_Wall_Mounted Craft 2TR SEER | Split_Wall_Mounted Carrier 2TR SEER 8.60
1052 | Split_Wall_Mounted | Ugine | KT3F-45W/J1 | Non-Inverter | 1.5 | 1.5 | 18000 | 0 |  | 0 | 0 |  |  | Split_Wall_Mounted Ugine 1.5TR SEER | Split_Wall_Mounted GREE 1.5TR SEER 9.98
1053 | Split_Wall_Mounted | LG | LS-D1821HM | Non-Inverter | 1.5 | 1.5 | 18000 | 1800 | 10 | 0 | 0 |  |  | Split_Wall_Mounted LG 1.5TR SEER | Split_Wall_Mounted GREE 1.5TR SEER 9.98
1054 | Split_Wall_Mounted | Kelvinator | HSCU18HB | Non-Inverter | 1.5 | 1.5 | 18000 | 2300 | 7.82 | 0 | 0 |  |  | Split_Wall_Mounted Kelvinator 1.5TR SEER | Split_Wall_Mounted Royal Temp 1.5TR SEER 7.67
1055 | Split_Wall_Mounted | Frego | FW24Y2M7 | Non-Inverter | 2 | 1.93 | 23202 | 2000 | 11.6 | 19899 | 2391.7067 | 8.32 | 9.86 | Split_Wall_Mounted Frego 1.93TR SEER 9.86 | Split_Wall_Mounted LG 1.74TR SEER 9.84
1056 | Split_Wall_Mounted | DANSAT | DSA24WC | Non-Inverter | 2 | 1.83 | 22000 | 1810 | 12.15 | 19000 | 1938.7755 | 9.8 | 10.65 | Split_Wall_Mounted DANSAT 1.83TR SEER 10.65 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
1057 | Split_Wall_Mounted | Mando | MP-18HD | Non-Inverter | 1.5 | 1.5 | 18000 | 1500 | 12 | 15600 | 1814 | 8.5998 | 10.2 | Split_Wall_Mounted Mando 1.5TR SEER 10.2 | Split_Wall_Mounted Ugine 1.48TR SEER 10.23
1058 | Split_Wall_Mounted | TIT | TAS-1815H6S-2 | Non-Inverter | 1.5 | 1.5 | 18000 | 1485 | 12.12 | 15600 | 1785 | 8.7395 | 10.32 | Split_Wall_Mounted TIT 1.5TR SEER 10.32 | Split_Wall_Mounted Mando 1.5TR SEER 10.35
1059 | Split_Wall_Mounted | CRONY | CRONY18CHL | Non-Inverter | 1.5 | 1.49 | 17913 | 1480 | 12.1 | 15354 | 1780 | 8.6258 | 10.27 | Split_Wall_Mounted CRONY 1.49TR SEER 10.27 | Split_Wall_Mounted Cooline 1.5TR SEER 10.25
1060 | Split_Wall_Mounted | York | YORX-18KC | Non-Inverter | 1.5 | 1.5 | 18000 | 1500 | 12 | 0 | 0 |  |  | Split_Wall_Mounted York 1.5TR SEER | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
1061 | Split_Wall_Mounted | Unistar | UNISTAR18SH | Non-Inverter | 1.5 | 1.5 | 18000 | 1500 | 12 | 0 | 0 |  |  | Split_Wall_Mounted Unistar 1.5TR SEER | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
1062 | Split_Wall_Mounted | York | YK9FXH018BAH-AX | Non-Inverter | 1.5 | 1.5 | 18000 | 1500 | 12 | 15500 | 0 |  |  | Split_Wall_Mounted York 1.5TR SEER | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
1063 | Split_Wall_Mounted | Luna | LAC-240KH | Non-Inverter | 2 | 2 | 24000 | 2750 | 8.72 | 0 | 0 |  |  | Split_Wall_Mounted Luna 2TR SEER | Split_Wall_Mounted Carrier 2TR SEER 8.60
1064 | Split_Wall_Mounted | Rantic | RTC18HN | Non-Inverter | 1.5 | 1.43 | 17197 | 1431 | 12.01 | 14899 | 1703 | 8.7487 | 10.26 | Split_Wall_Mounted Rantic 1.43TR SEER 10.26 | Split_Wall_Mounted Cooline 1.5TR SEER 10.25
1065 | Split_Wall_Mounted | Giant | ASTW-H18B2/EV | Non-Inverter | 1.5 | 1.5 | 18000 | 1940 | 9.27 | 16100 | 2370 | 6.7932 | 7.95 | Split_Wall_Mounted Giant 1.5TR SEER 7.95 | Split_Wall_Mounted LG 1.54TR SEER 8.14
1066 | Split_Wall_Mounted | Giant | ASTW-H12T2/ET-3 | Non-Inverter | 1 | 0.83 | 10000 | 1220 | 8.19 | 8750 | 1450 | 6.0345 | 7.02 | Split_Wall_Mounted Giant 0.83TR SEER 7.02 | Split_Wall_Mounted LG 0.95TR SEER 7.9
1067 | Split_Wall_Mounted | Queen | HOIT24H | Non-Inverter | 1.5 | 1.71 | 20523.18 | 2208 | 9.29 | 0 | 0 |  |  | Split_Wall_Mounted Queen 1.71TR SEER | Split_Wall_Mounted LG 1.82TR SEER 9.79
1068 | Split_Wall_Mounted | LG | S252LH | Non-Inverter | 2 | 2.04 | 24500 | 2450 | 10 | 0 | 0 |  |  | Split_Wall_Mounted LG 2.04TR SEER | Split_Wall_Mounted GREE 2.19TR SEER 10.05
1069 | Split_Wall_Mounted | Fuji | ROW-24RSD. | Non-Inverter | 1.5 | 1.62 | 19448.4 | 2900 | 6.7 | 0 | 0 |  |  | Split_Wall_Mounted Fuji 1.62TR SEER | Split_Wall_Mounted Gree 1.5TR SEER 7.03
1070 | Split_Wall_Mounted | York | YHGE12YT2BFER-3 | Non-Inverter | 1 | 1 | 12000 | 985 | 12.18 | 10050 | 0 |  |  | Split_Wall_Mounted York 1TR SEER | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
1071 | Split_Wall_Mounted | Ugne | UGNE-P24C-D | Non-Inverter | 2 | 1.84 | 22100 | 1811 | 12.2 | 18400 | 2152 | 8.5502 | 10.28 | Split_Wall_Mounted Ugne 1.84TR SEER 10.28 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
1072 | Split_Wall_Mounted | Midea | MSTG-18HR | Non-Inverter | 1.5 | 1.5 | 18000 | 2080 | 8.65 | 0 | 0 |  |  | Split_Wall_Mounted Midea 1.5TR SEER | Split_Wall_Mounted LG 1.5TR SEER 8.40
1073 | Split_Wall_Mounted | Arrow | MST2-30HR | Non-Inverter | 2.5 | 2.5 | 30000 | 2670 | 11.23 | 0 | 0 |  |  | Split_Wall_Mounted Arrow 2.5TR SEER | Split_Wall_Mounted Gree 2.25TR SEER 11.11
1074 | Split_Wall_Mounted | LUNA | LAC-180HK | Non-Inverter | 1.5 | 1.5 | 18000 | 2730 | 6.59 | 0 | 0 |  |  | Split_Wall_Mounted LUNA 1.5TR SEER | Split_Wall_Mounted LG 1.41TR SEER 6.94
1075 | Split_Wall_Mounted | Mando | MP-18CDN | Non-Inverter | 1.5 | 1.5 | 18000 | 1469 | 12.25 | 15200 | 1747 | 8.7006 | 10.37 | Split_Wall_Mounted Mando 1.5TR SEER 10.37 | Split_Wall_Mounted Okia 1.53TR SEER 10.37
1076 | Split_Wall_Mounted | Zamil | HAZ24CHXRDK | Non-Inverter | 2 | 1.85 | 22200 | 1827 | 12.15 | 19100 | 2220.9302 | 8.6 | 10.29 | Split_Wall_Mounted Zamil 1.85TR SEER 10.29 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
1077 | Split_Wall_Mounted | Zamil | HWX26EHAYPS | Non-Inverter | 2 | 2 | 24000 | 0 |  | 0 | 0 |  |  | Split_Wall_Mounted Zamil 2TR SEER | Split_Wall_Mounted Zamil 2TR SEER 10.39
1078 | Split_Wall_Mounted | Zamil | KXC24CSIHIST | Non-Inverter | 2 | 2 | 24000 | 0 |  | 0 | 0 |  |  | Split_Wall_Mounted Zamil 2TR SEER | Split_Wall_Mounted Zamil 2TR SEER 10.39
1079 | Split_Wall_Mounted | zamil | HWX24EHAXH | Non-Inverter | 2 | 2 | 24000 | 0 |  | 0 | 0 |  |  | Split_Wall_Mounted zamil 2TR SEER | Split_Wall_Mounted Zamil 2TR SEER 10.39
1080 | Split_Wall_Mounted | Zamil | MWZ24CHIXFT | Non-Inverter | 2 | 2 | 24000 | 0 |  | 0 | 0 |  |  | Split_Wall_Mounted Zamil 2TR SEER | Split_Wall_Mounted Zamil 2TR SEER 10.39
1081 | Split_Wall_Mounted | Zamil | CXC24C1HV8 | Non-Inverter | 2 | 2 | 24000 | 0 |  | 0 | 0 |  |  | Split_Wall_Mounted Zamil 2TR SEER | Split_Wall_Mounted Zamil 2TR SEER 10.39
1082 | Split_Wall_Mounted | LG | A122NC | Non-Inverter | 1 | 0.97 | 11737.28 | 1020 | 11.5 | 10021.044 | 0 |  |  | Split_Wall_Mounted LG 0.97TR SEER | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
1083 | Split_Wall_Mounted | Zamil | KXC26CSRHAPS | Non-Inverter | 2 | 2 | 24000 | 0 |  | 0 | 0 |  |  | Split_Wall_Mounted Zamil 2TR SEER | Split_Wall_Mounted Zamil 2TR SEER 10.39
1084 | Split_Wall_Mounted | LG | LST24CAG | Non-Inverter | 2 | 2 | 24000 | 2308 | 10.39 | 0 | 0 |  |  | Split_Wall_Mounted LG 2TR SEER | Split_Wall_Mounted Zamil 2TR SEER 10.39
1085 | Split_Wall_Mounted | Haier | HSU-24LNX13 | Non-Inverter | 2 | 1.83 | 22000 | 1795 | 12.25 | 19000 | 2222 | 8.5509 | 10.34 | Split_Wall_Mounted Haier 1.83TR SEER 10.34 | Split_Wall_Mounted Crown 1.79TR SEER 10.33
1086 | Split_Wall_Mounted | Samsung | ASH-2407BRX | Non-Inverter | 2 | 1.83 | 22000 | 2700 | 8.14 | 0 | 0 |  |  | Split_Wall_Mounted Samsung 1.83TR SEER | Split_Wall_Mounted LG 1.74TR SEER 8.17
1087 | Split_Wall_Mounted | Samsung | AR18MQFHCWKN | Non-Inverter | 1.5 | 1.45 | 17500 | 1500 | 11.66 | 15000 | 0 |  |  | Split_Wall_Mounted Samsung 1.45TR SEER | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
1088 | Split_Wall_Mounted | Gree | GWH12MB-D1NTA3A/O | Non-Inverter | 1 | 1 | 12000 | 1300 | 9.23 | 10200 | 1550 | 6.5806 | 7.82 | Split_Wall_Mounted Gree 1TR SEER 7.82 | Split_Wall_Mounted LG 0.95TR SEER 7.9
1089 | Split_Wall_Mounted | Midea | MSTG-30HR-I9 | Non-Inverter | 2.5 | 2.5 | 30000 | 3296.7033 | 9.1 | 0 | 0 |  |  | Split_Wall_Mounted Midea 2.5TR SEER | Split_Wall_Mounted Carrier 2.75TR SEER 8.81
1090 | Split_Wall_Mounted | Midea | MSTEP | Non-Inverter | 1.5 | 1.71 | 20545 | 1739 | 11.81 | 17577 | 2150 | 8.1753 | 9.94 | Split_Wall_Mounted Midea 1.71TR SEER 9.94 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
1091 | Split_Wall_Mounted | Midea | MSTE24CRNB2 | Non-Inverter | 2 | 1.95 | 23400 | 1900 | 12.31 | 19900 | 2280 | 8.7281 | 10.42 | Split_Wall_Mounted Midea 1.95TR SEER 10.42 | Split_Wall_Mounted Zamil 1.83TR SEER 10.42
1092 | Split_Wall_Mounted | Midea | MSTEP12HRN6 | Non-Inverter | 1 | 0.96 | 11529 | 983 | 11.72 | 9535 | 1125 | 8.4756 | 9.96 | Split_Wall_Mounted Midea 0.96TR SEER 9.96 | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
1093 | Split_Wall_Mounted | Ugine | UTS18USH | Non-Inverter | 1.5 | 1.5 | 18000 | 2250 | 8 | 0 | 0 |  |  | Split_Wall_Mounted Ugine 1.5TR SEER | Split_Wall_Mounted LG 1.54TR SEER 8.14
1094 | Split_Wall_Mounted | Ugine | UGNCC-24H7 | Non-Inverter | 2 | 1.99 | 23900 | 1960 | 12.19 | 20300 | 2350 | 8.6383 | 10.32 | Split_Wall_Mounted Ugine 1.99TR SEER 10.32 | Split_Wall_Mounted Mando 1.84TR SEER 10.28
1095 | Split_Wall_Mounted | GENERAL PLUS | GENP24CRS | Non-Inverter | 2 | 1.8 | 21600 | 1800 | 12 | 18400 | 2200 | 8.3636 | 10.11 | Split_Wall_Mounted GENERAL PLUS 1.8TR SEER 10.11 | Split_Wall_Mounted Carrier 1.83TR SEER 10.08
1096 | Split_Wall_Mounted | Kelvinator | GQR183MIO-M0 | Non-Inverter | 1.5 | 1.54 | 18500 | 0 |  | 0 | 0 |  |  | Split_Wall_Mounted Kelvinator 1.54TR SEER | Split_Wall_Mounted GREE 1.5TR SEER 9.98
1097 | Split_Wall_Mounted | GREE | GWH24MD-D1NTA8G/I | Non-Inverter | 2 | 1.83 | 22000 | 0 |  | 0 | 0 |  |  | Split_Wall_Mounted GREE 1.83TR SEER | Split_Wall_Mounted Zamil 2TR SEER 6.69
1098 | Split_Wall_Mounted | GREE | GWC18AGDXF-D3NTA1F/0 | Inverter | 1.5 | 1.54 | 18500 | 1492 | 12.39 | 0 | 0 |  |  | Split_Wall_Mounted GREE 1.54TR SEER | Inverter unit "No replacement"
1099 | Split_Wall_Mounted | GENERAL PLUS | GENPL24C | Non-Inverter | 1.5 | 1.5 | 18000 | 0 |  | 0 | 0 |  |  | Split_Wall_Mounted GENERAL PLUS 1.5TR SEER | Split_Wall_Mounted GREE 1.5TR SEER 9.98
1100 | Split_Wall_Mounted | FALCON | HNFC26HW-BG | Non-Inverter | 2 | 2 | 24000 | 2880 | 8.33 | 0 | 0 |  |  | Split_Wall_Mounted FALCON 2TR SEER | Split_Wall_Mounted Zamil 1.95TR SEER 8.11
1101 | Split_Wall_Mounted | Unionaire | HWC024U6HO | Non-Inverter | 2 | 1.96 | 23600 | 2472 | 9.54 | 0 | 0 |  |  | Split_Wall_Mounted Unionaire 1.96TR SEER | Split_Wall_Mounted Zamil 1.99TR SEER9.77
1102 | Split_Wall_Mounted | Fuji | RYT-24RSA | Non-Inverter | 1.5 | 1.5 | 18083.6 | 3000 | 6.02 | 0 | 0 |  |  | Split_Wall_Mounted Fuji 1.5TR SEER | Split_Wall_Mounted LG 1.41TR SEER 6.94
1103 | Split_Wall_Mounted | Haam | S-036C/hr | Non-Inverter | 2.5 | 2.43 | 29162 | 3480 | 8.37 | 24548 | 3800 | 6.46 | 7.25 | Split_Wall_Mounted Haam 2.43TR SEER 7.25 | Split_Wall_Mounted LG 2.25TR SEER 7.28
1104 | Split_Wall_Mounted | TACHIAIR | TCH30H/7S16 | Non-Inverter | 2 | 2 | 24000 | 2080 | 11.53 | 20500 | 2380 | 8.6134 | 9.91 | Split_Wall_Mounted TACHIAIR 2TR SEER 9.91 | Split_Wall_Mounted Carrier 1.92TR SEER 9.83
1105 | Split_Wall_Mounted | HAAS | HSA18CE6HGRC | Non-Inverter | 1.5 | 1.5 | 18083 | 2250 | 8.03 | 16200 | 2550 | 6.3529 | 7.03 | Split_Wall_Mounted HAAS 1.5TR SEER 7.03 | Split_Wall_Mounted LG 1.54TR SEER 8.14
1106 | Split_Wall_Mounted | Lakes | LSAC-18H/A | Non-Inverter | 1.5 | 1.4 | 16877.7 | 1890 | 8.93 | 14957.7 | 2190 | 6.83 | 7.74 | Split_Wall_Mounted Lakes 1.4TR SEER 7.74 | Split_Wall_Mounted Royal Temp 1.5TR SEER 7.67
1107 | Split_Wall_Mounted | Daikin | RY60GVAL | Non-Inverter | 2 | 2 | 24000 | 2610 | 9.19 | 0 | 0 |  |  | Split_Wall_Mounted Daikin 2TR SEER | Split_Wall_Mounted Zamil 1.99TR SEER9.77
1108 | Split_Wall_Mounted | Daikin | RY50GVAL | Non-Inverter | 1.5 | 1.64 | 19789.6 | 0 |  | 0 | 0 |  |  | Split_Wall_Mounted Daikin 1.64TR SEER | Split_Wall_Mounted Gree 1.5TR SEER 7.03
1109 | Split_Wall_Mounted | SPEEDCOOL | SKTS240H | Inverter | 2 | 1.8 | 21600 | 1742 | 12.39 | 0 | 0 |  |  | Split_Wall_Mounted SPEEDCOOL 1.8TR SEER | Inverter unit "No replacement"
1110 | Split_Wall_Mounted | SPEEDCOOL | ASC-18 | Non-Inverter | 1.5 | 1.5 | 18000 | 2100 | 8.57 | 0 | 0 |  |  | Split_Wall_Mounted SPEEDCOOL 1.5TR SEER | Split_Wall_Mounted LG 1.5TR SEER 8.40
1111 | Split_Wall_Mounted | SPEEDCOOL | SCIT18H | Non-Inverter | 1.5 | 1.41 | 16978.112 | 2040 | 8.32 | 14593.124 | 2409 | 6.0578 | 7.1 | Split_Wall_Mounted SPEEDCOOL 1.41TR SEER 7.1 | Split_Wall_Mounted LG 1.41TR SEER 6.94
1112 | Split_Wall_Mounted | TRIM | TRG12717OD | Non-Inverter | 1 | 0.95 | 11500 | 970 | 11.85 | 10200 | 1193 | 8.5499 | 10.12 | Split_Wall_Mounted TRIM 0.95TR SEER 10.12 | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
1113 | Split_Wall_Mounted | Coolsense | AAMJCSP18SAC | Non-Inverter | 1.5 | 1.5 | 18000 | 1480 | 12.16 | 16400 | 0 |  |  | Split_Wall_Mounted Coolsense 1.5TR SEER | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
1114 | Split_Wall_Mounted | Tcl | TAC-18CHS/MT2 | Non-Inverter | 1.5 | 1.5 | 18000 | 2000 | 9 | 0 | 0 |  |  | Split_Wall_Mounted Tcl 1.5TR SEER | Split_Wall_Mounted LG 1.5TR SEER 8.40
1115 | Split_Wall_Mounted | TCL | TAC-18CHS/ET2 | Non-Inverter | 1.5 | 1.33 | 16000 | 1900 | 8.42 | 0 | 0 |  |  | Split_Wall_Mounted TCL 1.33TR SEER | Split_Wall_Mounted LG 1.46TR SEER 7.57
1116 | Split_Wall_Mounted | Luna | LAC-180KHF | Non-Inverter | 1.5 | 1.5 | 18000 | 2400 | 7.5 | 0 | 0 |  |  | Split_Wall_Mounted Luna 1.5TR SEER | Split_Wall_Mounted LG 1.46TR SEER 7.56
1117 | Split_Wall_Mounted | Class pro | CLS18H8SEC | Non-Inverter | 1.5 | 1.48 | 17800 | 1460 | 12.19 | 15400 | 0 |  |  | Split_Wall_Mounted Class pro 1.48TR SEER | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
1118 | Split_Wall_Mounted | SKM | FZW-020HP | Non-Inverter | 1.5 | 1.52 | 18300 | 0 |  | 0 | 0 |  |  | Split_Wall_Mounted SKM 1.52TR SEER | Split_Wall_Mounted GREE 1.5TR SEER 9.98
1119 | Split_Wall_Mounted | AUX | AUX24CHD | Inverter | 2 | 2 | 24000 | 1930 | 12.43 | 20000 | 2285.7143 | 8.75 | 10.49 | Split_Wall_Mounted AUX 2TR SEER 10.49 | Inverter unit "No replacement"
1120 | Split_Wall_Mounted | Craft | SXSA18CF73H | Non-Inverter | 1.5 | 1.5 | 18000 | 0 |  | 0 | 0 |  |  | Split_Wall_Mounted Craft 1.5TR SEER | Split_Wall_Mounted GREE 1.5TR SEER 9.98
1121 | Split_Wall_Mounted | WBOX | WBAC18IH | Non-Inverter | 1.5 | 1.44 | 17300 | 1450 | 11.93 | 14700 | 1710 | 8.5965 | 10.14 | Split_Wall_Mounted WBOX 1.44TR SEER 10.14 | Split_Wall_Mounted LG 1.47TR SEER 10.15
1122 | Split_Wall_Mounted | Arrow | RO-18SMC | Non-Inverter | 1.5 | 1.5 | 18000 | 1469 | 12.25 | 15200 | 1747 | 8.7006 | 10.37 | Split_Wall_Mounted Arrow 1.5TR SEER 10.37 | Split_Wall_Mounted Okia 1.53TR SEER 10.37
1123 | Split_Wall_Mounted | UNIX | MUNIXSp-24CN | Non-Inverter | 1.5 | 1.79 | 21500 | 1820 | 11.81 | 18300 | 2180 | 8.3945 | 10.01 | Split_Wall_Mounted UNIX 1.79TR SEER 10.01 | Split_Wall_Mounted Carrier 1.83TR SEER 10.08
1124 | Split_Wall_Mounted | Comfort | MSAC-30CHS/GT7 | Non-Inverter | 2 | 2.04 | 24500 | 2110 | 11.61 | 0 | 0 |  |  | Split_Wall_Mounted Comfort 2.04TR SEER | Split_Wall_Mounted Zamil 2TR SEER 10.39
1125 | Split_Wall_Mounted | Super_General | KSGS241GER | Non-Inverter | 1.5 | 1.75 | 21000 | 1721 | 12.2 | 19200 | 2207 | 8.6996 | 10.4 | Split_Wall_Mounted Super_General 1.75TR SEER 10.4 | Split_Wall_Mounted Arrow 1.75TR SEER 10.39
1126 | Split_Floor_Standing | Ugine | KT3FR-120W/lE | Non-Inverter | 3.5 | 3.41 | 41025.641 | 4990 | 8.22 | 0 | 0 |  |  | Split_Floor_Standing Ugine 3.41TR SEER | Split_Floor_Standing Zamil 3.42TR SEER 6.87
1127 | Split_Ceiling_Cassette | LG | ATU1W18GPL | Non-Inverter | 1.5 | 1.49 | 17981.24 | 1550 | 11.6 | 15456.36 | 1710 | 9.0388 | 10.08 | Split_Ceiling_Cassette LG 1.49TR SEER 10.08 | Split_Ceiling_Cassette LG 1.5TR SEER 8.05
1128 | Split_Ceiling_Cassette | Gree | gutd24w4/a-s | Non-Inverter | 2 | 2 | 24000 | 0 |  | 0 | 0 |  |  | Split_Ceiling_Cassette Gree 2TR SEER | Split_Ceiling_Cassette Mitsubishi 2.02TR SEER 6.93
1129 | Split_Ceiling_Cassette | Carrier | 38DPJ024-323F-C | Non-Inverter | 2 | 2 | 24000 | 2900 | 8.27 | 0 | 0 |  |  | Split_Ceiling_Cassette Carrier 2TR SEER | Split_Ceiling_Cassette LG 1.99TR SEER 8.23
1130 | Split_Ceiling_Cassette | Royal_Temp | RT Casette | Non-Inverter | 2 | 2 | 24000 | 0 |  | 0 | 0 |  |  | Split_Ceiling_Cassette Royal_Temp 2TR SEER | Split_Ceiling_Cassette Mitsubishi 2.02TR SEER 6.93
1131 | Split_Ceiling_Cassette | Gree | GUTD36W/A | Non-Inverter | 3 | 3 | 36000 | 0 |  | 0 | 0 |  |  | Split_Ceiling_Cassette Gree 3TR SEER | Split_Ceiling_Cassette Carrier 2.88TR SEER 10.05
1132 | Split_Ceiling_Cassette | Zamil | KXC24CSIHAAW | Non-Inverter | 2 | 2 | 24000 | 0 |  | 0 | 0 |  |  | Split_Ceiling_Cassette Zamil 2TR SEER | Split_Ceiling_Cassette Mitsubishi 2.02TR SEER 6.93
1133 | Split_Ceiling_Cassette | Carrier | 38CK048-X-3A1 | Non-Inverter | 4 | 4 | 48000 | 0 |  | 0 | 0 |  |  | Split_Ceiling_Cassette Carrier 4TR SEER | Split_Ceiling_Cassette LG 4.21TR SEER 7.69
1134 | Split_Ceiling_Cassette | General | AOS25R2AL | Non-Inverter | 1.5 | 1.59 | 19107.2 | 2250 | 8.49 | 0 | 0 |  |  | Split_Ceiling_Cassette General 1.59TR SEER | Split_Ceiling_Cassette LG 1.5TR SEER 8.05
1135 | Window | Zamil | HHB24CKERIMNW | Non-Inverter | 2 | 1.85 | 22250 | 2602 | 8.55 | 18500 | 3008 | 6.1503 | 7.25 | Window Zamil 1.85TR SEER 7.25 | Window Zamil 2TR SEER 7.24
1136 | Window | Zamil | ZHB24CPEQIMNW | Non-Inverter | 1.5 | 1.79 | 21500 | 2870 | 7.49 | 18000 | 3300 | 5.4545 | 6.37 | Window Zamil 1.79TR SEER 6.37 | Window Zamil 1.79TR SEER 6.38
1137 | Window | Haam | HW18E3WC | Non-Inverter | 1.5 | 1.5 | 18000 | [5 empty] | 6.72 | Window Haam 1.5TR SEER 6.72 | Window Zamil 1.5TR SEER 6.51
1138 | Window | White Westinghouse | WGS-240-C/H | Non-Inverter | 2 | 2 | 24000 | [5 empty] | 6.4 | Window White Westinghouse 2TR SEER 6.4 | Window Zamil 2TR SEER 6.23
1139 | Window | Craft | DE24E8JT41 | Non-Inverter | 2 | 2.01 | 24200 | [5 empty] | 7.67 | Window Craft 2.01TR SEER 7.67 | Window Carrier 2.01TR SEER 7.59
1140 | Window | Falcon | FSSR243M-0G8 | Non-Inverter | 1.5 | 1.75 | 21000 | [5 empty] | 8.45 | Window Falcon 1.75TR SEER 8.45 | Window York 1.75TR SEER 8.45
1141 | Window | Haam | HMVD183M-5B-17 | Non-Inverter | 1.5 | 1.5 | 18100 | [5 empty] | 8.25 | Window Haam 1.5TR SEER 8.25 | Window Zamil 1.5TR SEER 6.51
1142 | Window | Kelvinator | KSSD183M-0K8 | Non-Inverter | 1.5 | 1.48 | 17800 | [5 empty] | 8.37 | Window Kelvinator 1.48TR SEER 8.37 | Window Zamil 1.5TR SEER 6.51
1143 | Window | LG | W242SR SN0 /GWH242NAMM0 | Non-Inverter | 2 | 2 | 24000 | [5 empty] | 7.25 | Window LG 2TR SEER 7.25 | Window Zamil 2TR SEER 7.24
1144 | Split_Wall_Mounted | Midea | MSTM18HRN2/MSTM18HRN2 | Non-Inverter | 1.5 | 1.54 | 18500 | [5 empty] | 10.05 | Split_Wall_Mounted Midea 1.54TR SEER 10.05 | Split_Wall_Mounted Cooline 1.5TR SEER 10.25
1145 | Window | National | W18CTM | Non-Inverter | 1.5 | 1.47 | 17640 | [6 empty] | Window National 1.47TR SEER | Window Carrier 1.43TR SEER 8.52
1146 | Window | Starway | WYR18KHC | Non-Inverter | 1.5 | 1.45 | 17400 | [5 empty] | 8.44 | Window Starway 1.45TR SEER 8.44 | Window Carrier 1.43TR SEER 8.52
1147 | Window | Toshiba | RAC-24B-Q | Non-Inverter | 2 | 1.83 | 22000 | [5 empty] | 7.26 | Window Toshiba 1.83TR SEER 7.26 | Window Zamil 2TR SEER 7.24
1148 | Window | York | LYSD243M-0C8 | Non-Inverter | 2 | 2.01 | 24200 | 2674 | 9.05 | 18700 | 2968 | 6.3005 | 7.57 | Window York 2.01TR SEER 7.57 | Window Zamil 2TR SEER 7.24
1149 | Window | York | LYSD243M-0B5 | Non-Inverter | 2 | 2 | 24050 | 2813 | 8.54 | 18970 | 3089 | 6.1411 | 7.22 | Window York 2TR SEER 7.22 | Window Zamil 2TR SEER 7.24
1150 | Window | Zamil | YHB1BCTEYIINW | Non-Inverter | 1.5 | 1.5 | 18000 | [5 empty] | 6.8 | Window Zamil 1.5TR SEER 6.8 | Window Samsung 1.5TR SEER 6.82
1151 | Window | Zamil | HHB19CKERIMNW | Non-Inverter | 1.5 | 1.58 | 19000 | [5 empty] | 7.21 | Window Zamil 1.58TR SEER 7.21 | Window LG 1.49TR SEER 7.24
1152 | Window | Zamil | AHM24CEBW | Non-Inverter | 2 | 2 | 24000 | [5 empty] | 7.04 | Window Zamil 2TR SEER 7.04 | Window Zamil 2TR SEER 7.24
1153 | Window | Craft | D024E8H5Y | Non-Inverter | 2 | 2 | 24005 | 2805 | 8.55 | 20499.2892 | 3345 | 6.1283 | 7.26 | Window Craft 2TR SEER 7.26 | Window Zamil 2TR SEER 7.24
1154 | Window | Kelvinator | KSVR243M-1 | Non-Inverter | 2 | 2 | 24000 | 2700 | 8.88 | 18493.0338 | 3100 | 5.9655 | 7.36 | Window Kelvinator 2TR SEER 7.36 | Window Zamil 2TR SEER 7.33
1155 | Window | Haas | H024E8H5YX | Non-Inverter | 2 | 2 | 24000 | 2805 | 8.55 | 20499.2892 | 3345 | 6.1283 | 7.26 | Window Haas 2TR SEER 7.26 | Window Zamil 2TR SEER 7.24
1156 | Window | Haas | HO125E8Y | Non-Inverter | 2 | 1.83 | 22000 | 2155 | 10.2 | 18500 | 2570 | 7.1984 | 8.62 | Window Haas 1.83TR SEER 8.62 | Window York 1.75TR SEER 8.45
1157 | Window | Fisher | FWAC-T18CE | Non-Inverter | 1.5 | 1.41 | 17000 | 1650 | 10.3 | 13700 | 1943 | 7.051 | 8.6 | Window Fisher 1.41TR SEER 8.6 | Window Carrier 1.5TR SEER 8.62
1158 | Window | Zamil | ACB24CTEAIMNW | Non-Inverter | 2 | 2 | 24000 | 2740 | 8.75 | 18000 | 3200 | 5.625 | 7.15 | Window Zamil 2TR SEER 7.15 | Window Zamil 2TR SEER 7.20
1159 | Window | Zamil | AHM24CEA | Non-Inverter | 2 | 2 | 24000 | 2800 | 8.57 | 18000 | 3500 | 5.1429 | 6.86 | Window Zamil 2TR SEER 6.86 | Window Zamil 2TR SEER 6.95
1160 | Window | LG | E182BH SN0 | Non-Inverter | 1.5 | 1.48 | 17878.874 | 1820 | 9.82 | 15353.9949 | 2170 | 7.0756 | 8.35 | Window LG 1.48TR SEER 8.35 | Window Carrier 1.43TR SEER 8.52
1161 | Window | Gibson | AE24E6H5JN | Non-Inverter | 2 | 2.02 | 24300 | 2820 | 8.61 | 19500 | 3180 | 6.1321 | 7.26 | Window Gibson 2.02TR SEER 7.26 | Window Zamil 1.88TR SEER 7.28
1162 | Window | Zamil | AHM24CEB | Non-Inverter | 2 | 2 | 24000 | 2300 | 10.43 | 18000 | 3200 | 5.625 | 8.09 | Window Zamil 2TR SEER 8.09 | Window LG 2TR SEER 7.48
1163 | Window | Carrier | 51GVR243M 1S | Non-Inverter | 2 | 1.83 | 22000 | 2430 | 9.05 | 18970.7137 | 3000 | 6.3236 | 7.63 | Window Carrier 1.83TR SEER 7.63 | Window LG 2TR SEER 7.48
1164 | Window | York | NYVD183M-0C | Non-Inverter | 1.5 | 1.5 | 18000 | 2200 | 8.18 | 14978.675 | 2500 | 5.9915 | 6.97 | Window York 1.5TR SEER 6.97 | Window Zamil 1.5TR SEER 6.92
1165 | Window | Zamil | AHB26CHELKINW | Non-Inverter | 2 | 2 | 24000 | 2810 | 8.54 | 18000 | 3120 | 5.7692 | 7.07 | Window Zamil 2TR SEER 7.07 | Window Zamil 2TR SEER 7.10
1166 | Window | Super_General | KSGA24GE | Non-Inverter | 1.5 | 1.66 | 20000 | 1942 | 10.29 | 16100 | 2284 | 7.049 | 8.6 | Window Super_General 1.66TR SEER 8.6 | Window York 1.75TR SEER 8.45
1167 | Window | TCL | CW-TW18CW1 | Non-Inverter | 1.5 | 1.5 | 18000 | 1800 | 10 | 15200 | 2156 | 7.0501 | 8.44 | Window TCL 1.5TR SEER 8.44 | Window Carrier 1.43TR SEER 8.52
1168 | Window | Frego | FT18E2H9 | Non-Inverter | 1.5 | 1.45 | 17500 | 1710 | 10.23 | 14500 | 2040 | 7.1078 | 8.59 | Window Frego 1.45TR SEER 8.59 | Window Carrier 1.5TR SEER 8.62
1169 | Window | Gree | GJC24AE-D3NMTD5D | Non-Inverter | 2 | 1.81 | 21800 | 2150 | 10.13 | 18300 | 2550 | 7.1765 | 8.57 | Window Gree 1.81TR SEER 8.57 | Window York 1.75TR SEER 8.45
1170 | Window | Zamil | AHM18CEA | Non-Inverter | 1.5 | 1.5 | 18000 | 2100 | 8.57 | 15000 | 2400 | 6.25 | 7.29 | Window Zamil 1.5TR SEER 7.29 | Window LG 1.49TR SEER 7.24
1171 | Window | Ugine | UGNW18C-5 | Non-Inverter | 1.5 | 1.48 | 17800 | 1787 | 9.96 | 15000 | 2117 | 7.0855 | 8.43 | Window Ugine 1.48TR SEER 8.43 | Window Carrier 1.43TR SEER 8.52
1172 | Window | General | ANJ24BDG1R | Non-Inverter | 2 | 2 | 24050 | 2813 | 8.54 | 20000 | 3268 | 6.12 | 7.24 | Window General 2TR SEER 7.24 | Window Zamil 2TR SEER 7.24
1173 | Window | Carrier | C2K5G-18HK5 | Non-Inverter | 1.5 | 1.5 | 18000 | 2300 | 7.82 | 14193.9153 | 2750 | 5.1614 | 6.46 | Window Carrier 1.5TR SEER 6.46 | Window Zamil 1.5TR SEER 6.51
1174 | Window | Zamil | AHB19CIEPIMNW | Non-Inverter | 1.5 | 1.54 | 18500 | 2260 | 8.18 | 14000 | 2510 | 5.5777 | 6.8 | Window Zamil 1.54TR SEER 6.8 | Window Zamil 1.5TR SEER 6.80
1175 | Window | Carrier | CACH24 | Non-Inverter | 2 | 2 | 24000 | 2970 | 8.08 | 18697.7538 | 3500 | 5.3422 | 6.67 | Window Carrier 2TR SEER 6.67 | Window Royal Temp 2TR SEER 6.41
1176 | Window | Carrier | C2K18HK5 | Non-Inverter | 1.5 | 1.5 | 18000 | 2450 | 7.34 | 14630 | 2750 | 5.32 | 6.23 | Window Carrier 1.5TR SEER 6.23 | Window Zamil 1.5TR SEER 6.51
1177 | Window | Carrier | 51GVD3324-3 | Non-Inverter | 2 | 2 | 24000 | 3400 | 7.05 | 18493.0338 | 3770 | 4.9053 | 5.9 | Window Carrier 2TR SEER 5.9 | Window Zamil 2TR SEER 6.23
1178 | Split_Floor_Standing | Gree | KT3F-120LW/E | Non-Inverter | 4 | 4 | 48000 | [6 empty] | Split_Floor_Standing Gree 4TR SEER | Split_Floor_Standing LG 4.35TR SEER 7.05
1179 | Split_Floor_Standing | Samsung | AP55M2AN | Non-Inverter | 4 | 4.16 | 50000 | [5 empty] | 7.84 | Split_Floor_Standing Samsung 4.16TR SEER 7.84 | Split_Floor_Standing LG 4.35TR SEER 7.05
1180 | Split_Floor_Standing | Rheem | RFS48CMTSCR1 | Non-Inverter | 4 | 3.85 | 46200 | [5 empty] | 9.91 | Split_Floor_Standing Rheem 3.85TR SEER 9.91 | Split_Floor_Standing LG 3.75TR SEER 7.47
1181 | Split_Floor_Standing | Samsung | AP55Q0DN | Non-Inverter | 4.5 | 4.33 | 52000 | [5 empty] | 8.23 | Split_Floor_Standing Samsung 4.33TR SEER 8.23 | Split_Floor_Standing LG 4.35TR SEER 7.05
1182 | Split_Floor_Standing | LG | LP-C552TM3 | Non-Inverter | 3 | 3.15 | 37873.1874 | 4100 | 9.23 | 32072.7893 | 4800 | 6.6818 | 7.86 | Split_Floor_Standing LG 3.15TR SEER 7.86 | Split_Floor_Standing LG 3.15TR SEER 7.86
1183 | Split_Floor_Standing | Winner | FS-050CHR | Non-Inverter | 4 | 3.83 | 46061.9846 | 5470 | 8.42 | 42308.7859 | 6380 | 6.6315 | 7.37 | Split_Floor_Standing Winner 3.83TR SEER 7.37 | Split_Floor_Standing LG 3.75TR SEER 7.47
1184 | Split_Floor_Standing | LG | LP-C552TE2 | Non-Inverter | 3.5 | 3.32 | 39920.3867 | 4690 | 8.51 | 33096.389 | 5400 | 6.129 | 7.22 | Split_Floor_Standing LG 3.32TR SEER 7.22 | Split_Floor_Standing LG 3.32TR SEER 7.22
1185 | Split_Floor_Standing | Ugine | UGNFL-60C7 | Non-Inverter | 5.5 | 4.35 | 52200 | 4410 | 11.83 | 48500 | 5470 | 8.8665 | 10.24 | Split_Floor_Standing Ugine 4.35TR SEER 10.24 | Split_Floor_Standing Samsung 4TR SEER 10.3
1186 | Split_Floor_Standing | Carrier | 42HD7B / 38CKC060 | Non-Inverter | 5 | 5 | 60000 | 5600 | 10.71 | 0 | 0 |  | - | Split_Floor_Standing Carrier 5TR SEER - | Split_Floor_Standing LG 4.5TR SEER 10.00
1187 | Split_Floor_Standing | Carrier | 42HD6B / 38CKC048 | Non-Inverter | 4 | 4 | 48000 | 8251 | 5.81 | 0 | 0 |  | - | Split_Floor_Standing Carrier 4TR SEER - | Split_Floor_Standing LG 4.35TR SEER 7.05
1188 | Split_Floor_Standing | LG | LP-H552TM2 | Non-Inverter | 3.5 | 3.72 | 44697.1851 | 4930 | 9.06 | 37531.9875 | 5860 | 6.4048 | 7.65 | Split_Floor_Standing LG 3.72TR SEER 7.65 | Split_Floor_Standing LG 3.72TR SEER 7.65
1189 | Split_Floor_Standing | Century | KPC-48/7S | Non-Inverter | 3 | 3.01 | 36167.1879 | 3137 | 11.52 | 32413.9892 | 3900 | 8.3113 | 9.84 | Split_Floor_Standing Century 3.01TR SEER 9.84 | Split_Floor_Standing Daewoo 3.16TR SEER 8.11
1190 | Split_Floor_Standing | LG | LP-C552TE1 | Non-Inverter | 5 | 4.58 | 55000 | 4200 | 13.09 | 0 | 0 |  | - | Split_Floor_Standing LG 4.58TR SEER - | Split_Floor_Standing Zamil 4.421TR SEER 10.15
1191 | Split_Floor_Standing | Awalgulf | EQ048SCAC | Non-Inverter | 4 | 4 | 48000 | 6380 | 7.52 | 41280 | 6440 | 6.4099 | 6.68 | Split_Floor_Standing Awalgulf 4TR SEER 6.68 | Split_Floor_Standing LG 4.35TR SEER 7.05
1192 | Split_Floor_Standing | York | YE8FT55SH7AC41 | Non-Inverter | 4.5 | 4.25 | 51000 | 4322 | 11.8 | 45000 | 5357 | 8.4002 | 10.03 | Split_Floor_Standing York 4.25TR SEER 10.03 | Split_Floor_Standing LG 4.5TR SEER 10.00
1193 | Split_Ceiling_Cassette | York | YE3CJ24SC7AC22 | Non-Inverter | 3 | 2 | 24000 | 3190 | 7.52 | 20640 | 3800 | 5.4316 | 6.41 | Split_Ceiling_Cassette York 2TR SEER 6.41 | Split_Ceiling_Cassette Mitsubishi 2.02TR SEER 6.93
1194 | Split_Ceiling_Cassette | Samsung | AF55MV1MAEEN | Non-Inverter | 4 | 4 | 48000 | 4050 | 11.85 | 42000 | 4920 | 8.5366 | 10.1 | Split_Ceiling_Cassette Samsung 4TR SEER 10.1 | Split_Ceiling_Cassette LG 3.83TR SEER 9.87
1195 | Split_Ceiling_Cassette | Sky star | C-24C | Non-Inverter | 3 | 2 | 24000 | 2030 | 11.82 | 20000 | 2350 | 8.5106 | 10.03 | Split_Ceiling_Cassette Sky star 2TR SEER 10.03 | Split_Ceiling_Cassette Carrier 1.96TR SEER 10.25
1196 | Split_Ceiling_Cassette | York | YE7CT24SH7AC41 | Non-Inverter | 3 | 1.85 | 22200 | 1914 | 11.59 | 20000 | 2381 | 8.3998 | 9.92 | Split_Ceiling_Cassette York 1.85TR SEER 9.92 | Split_Ceiling_Cassette Carrier 1.96TR SEER 10.25
1197 | Split_Ceiling_Cassette | York | YE3CM30SC7AC22 | Non-Inverter | 2.5 | 2.5 | 30000 | 3990 | 7.51 | 25800 | 4770 | 5.4088 | 6.39 | Split_Ceiling_Cassette York 2.5TR SEER 6.39 | Split_Ceiling_Cassette LG 2.31TR SEER 7.39
1198 | Split_Ceiling_Cassette | Craft | DS24FE7HY7KM | Non-Inverter | 2 | 1.93 | 23200 | 1933 | 12 | 20000 | 2353 | 8.4998 | 10.17 | Split_Ceiling_Cassette Craft 1.93TR SEER 10.17 | Split_Ceiling_Cassette Carrier 1.96TR SEER 10.25
1199 | Split_Ceiling_Cassette | York | YE3SD240SCAW22 | Non-Inverter | 2 | 2 | 24000 | 3190 | 7.52 | 20640 | 3810 | 5.4173 | 6.4 | Split_Ceiling_Cassette York 2TR SEER 6.4 | Split_Ceiling_Cassette Mitsubishi 2.02TR SEER 6.93
1200 | Split_Ceiling_Cassette | Craft | DS36FE7HS7KM2 | Non-Inverter | 2.5 | 2.7 | 32400 | 2655 | 12.2 | 27000 | 3175 | 8.5039 | 10.27 | Split_Ceiling_Cassette Craft 2.7TR SEER 10.27 | Split_Ceiling_Cassette Carrier 2.88TR SEER 10.05
1201 | Split_Ceiling_Cassette | York | YE8CT24SH7AC41 | Non-Inverter | 2 | 1.85 | 22200 | 1850 | 12 | 19600 | 2306 | 8.4996 | 10.18 | Split_Ceiling_Cassette York 1.85TR SEER 10.18 | Split_Ceiling_Cassette Carrier 1.96TR SEER 10.25
1202 | Split_Ceiling_Cassette | GREE | GUD18T/A1-S(S) | Non-Inverter | 1.5 | 1.51 | 18200 | 1515 | 12.01 | 16800 | 2000 | 8.4 | 10.19 | Split_Ceiling_Cassette GREE 1.51TR SEER 10.19 | Split_Ceiling_Cassette LG 1.5TR SEER 8.05
1203 | Split_Ceiling_Cassette | York | YE6CT18SC7BC41 | Non-Inverter | 1.5 | 1.42 | 17100 | 1482 | 11.53 | 15390 | 1852 | 8.3099 | 9.85 | Split_Ceiling_Cassette York 1.42TR SEER 9.85 | Split_Ceiling_Cassette Carrier 1.33TR SEER 10.51
1204 | Split_Ceiling_Cassette | Midea | MCCTV30HRN2 | Inverter | 2 | 2.25 | 27000 | 2160 | 12.5 | 24200 | 2750 | 8.8 | 10.6 | Split_Ceiling_Cassette Midea 2.25TR SEER 10.6 | Inverter unit "No replacement"
1205 | Split_Wall_Mounted | Craft | DSA25CE7GR7 | Non-Inverter | 2 | 1.87 | 22500 | [5 empty] | 10.06 | Split_Wall_Mounted Craft 1.87TR SEER 10.06 | Split_Wall_Mounted Zamil 2TR SEER 6.69
1206 | Split_Wall_Mounted | General | AWS18ABAJ | Non-Inverter | 1.5 | 1.3 | 15695 | [6 empty] | Split_Wall_Mounted General 1.3TR SEER | Split_Wall_Mounted LG 1.41TR SEER 6.94
1207 | Split_Wall_Mounted | General | ASSA24RAT | Non-Inverter | 2 | 1.88 | 22600 | [5 empty] | 7.71 | Split_Wall_Mounted General 1.88TR SEER 7.71 | Split_Wall_Mounted Zamil 2TR SEER 6.69
1208 | Split_Wall_Mounted | General | ASS30ABAJ | Non-Inverter | 2 | 1.91 | 23001 | [6 empty] | Split_Wall_Mounted General 1.91TR SEER | Split_Wall_Mounted Zamil 2TR SEER 6.69
1209 | Split_Wall_Mounted | Haam | HM30C/7S17 | Non-Inverter | 2 | 1.89 | 22770 | [5 empty] | 9.88 | Split_Wall_Mounted Haam 1.89TR SEER 9.88 | Split_Wall_Mounted Zamil 2TR SEER 6.69
1210 | Split_Wall_Mounted | LG | T182NC / LSNQ182CNC0 | Non-Inverter | 1.5 | 1.47 | 17742 | [5 empty] | 9.86 | Split_Wall_Mounted LG 1.47TR SEER 9.86 | Split_Wall_Mounted LG 1.41TR SEER 6.94
1211 | Split_Wall_Mounted | LG | S242NH / GSNH2425NB2 | Non-Inverter | 2 | 1.91 | 22996 | [5 empty] | 7.54 | Split_Wall_Mounted LG 1.91TR SEER 7.54 | Split_Wall_Mounted Zamil 2TR SEER 6.69
1212 | Split_Wall_Mounted | LG | S3220C | Non-Inverter | 2.5 | 2.66 | 32000 | [6 empty] | Split_Wall_Mounted LG 2.66TR SEER | Split_Wall_Mounted Royal Temp 2.67TR SEER 7.44
1213 | Split_Wall_Mounted | Samsung | AS24UUPX | Non-Inverter | 2 | 2 | 24000 | [5 empty] | 7.37 | Split_Wall_Mounted Samsung 2TR SEER 7.37 | Split_Wall_Mounted Zamil 2TR SEER 6.69
1214 | Split_Wall_Mounted | Samsung | UST24A6RB | Non-Inverter | 2 | 2 | 24000 | [5 empty] | 7.87 | Split_Wall_Mounted Samsung 2TR SEER 7.87 | Split_Wall_Mounted Zamil 2TR SEER 6.69
1215 | Split_Wall_Mounted | Zamil | YMCVD0304M | Non-Inverter | 2 | 1.98 | 23799 | [5 empty] | 8.14 | Split_Wall_Mounted Zamil 1.98TR SEER 8.14 | Split_Wall_Mounted Zamil 2TR SEER 6.69
1216 | Split_Wall_Mounted | LG | T3224H | Non-Inverter | 2 | 2.33 | 27978.3907 | 2320 | 12.05 | 24600.5118 | 2650 | 9.2832 | 10.46 | Split_Wall_Mounted LG 2.33TR SEER 10.46 | Split_Wall_Mounted LG 2.33TR SEER 10.46
1217 | Split_Wall_Mounted | LG | Y242NH | Non-Inverter | 1.5 | 1.74 | 20949.673 | 2200 | 9.52 | 18254.1939 | 2550 | 7.1585 | 8.2 | Split_Wall_Mounted LG 1.74TR SEER 8.2 | Split_Wall_Mounted LG 1.74TR SEER 8.20
1218 | Split_Wall_Mounted | Craft | DSW30FE7HY7M | Non-Inverter | 2 | 2.37 | 28500 | 2342 | 12.16 | 23870.344 | 2790 | 8.5557 | 10.26 | Split_Wall_Mounted Craft 2.37TR SEER 10.26 | Split_Wall_Mounted Carrier 2.25TR SEER 10.20
1219 | Split_Wall_Mounted | Haas | HSA25FE6HH7X | Non-Inverter | 2 | 1.91 | 23000 | 1925 | 11.94 | 19800 | 2290 | 8.6463 | 10.17 | Split_Wall_Mounted Haas 1.91TR SEER 10.17 | Split_Wall_Mounted Gree 1.83TR SEER 10.17
1220 | Split_Wall_Mounted | Samsung | AQ24FCN | Non-Inverter | 2 | 2 | 24000 | 2650 | 9.05 | 19828.35 | 3100 | 6.3962 | 7.64 | Split_Wall_Mounted Samsung 2TR SEER 7.64 | Split_Wall_Mounted Royal Temp 2TR SEER 7.64
1221 | Split_Wall_Mounted | Yoko | YOKO-36FCH | Non-Inverter | 2.5 | 2.53 | 30400 | 2500 | 12.16 | 26000 | 3000 | 8.6667 | 10.31 | Split_Wall_Mounted Yoko 2.53TR SEER 10.31 | Split_Wall_Mounted Carrier 2.58TR SEER 10.41
1222 | Split_Wall_Mounted | York | YE3SD30RSHYW22 | Non-Inverter | 2.5 | 2.5 | 30000 | 3990 | 7.51 | 25800 | 4750 | 5.4316 | 6.4 | Split_Wall_Mounted York 2.5TR SEER 6.4 | Split_Wall_Mounted Royal Temp 2.5TR SEER 7.53
1223 | Split_Wall_Mounted | LG | T3624C | Non-Inverter | 2.5 | 2.58 | 31015.0697 | 2710 | 11.44 | 24805.2317 | 2960 | 8.3801 | 9.72 | Split_Wall_Mounted LG 2.58TR SEER 9.72 | Split_Wall_Mounted LG 2.58TR SEER 9.72
1224 | Split_Wall_Mounted | Falcon | FSEH24 | Non-Inverter | 2 | 2 | 24000 | 2970 | 8.08 | 18697.7538 | 3500 | 5.3422 | 6.66 | Split_Wall_Mounted Falcon 2TR SEER 6.66 | Split_Wall_Mounted Zamil 2TR SEER 6.69
1225 | Split_Wall_Mounted | LG | T3624H | Non-Inverter | 2.5 | 2.58 | 31015.0697 | 2720 | 11.4 | 24771.1117 | 2920 | 8.4833 | 9.72 | Split_Wall_Mounted LG 2.58TR SEER 9.72 | Split_Wall_Mounted LG 2.58TR SEER 9.73
1226 | Split_Wall_Mounted | Mando | AC-24H-MDE | Non-Inverter | 2 | 1.93 | 23202 | 2000 | 11.6 | 19899 | 2390 | 8.3259 | 9.85 | Split_Wall_Mounted Mando 1.93TR SEER 9.85 | Split_Wall_Mounted LG 1.74TR SEER 9.84
1227 | Split_Wall_Mounted | Ugine | UGNE-P30CH-DN | Non-Inverter | 2 | 2.23 | 26800 | 2197 | 12.19 | 22600 | 2613 | 8.6491 | 10.31 | Split_Wall_Mounted Ugine 2.23TR SEER 10.31 | Split_Wall_Mounted Zamil 2.24TR SEER 10.35
1228 | Split_Wall_Mounted | Samsung | AQ18FCN | Non-Inverter | 1.5 | 1.5 | 18000 | 1900 | 9.47 | 15267.8295 | 2250 | 6.7857 | 8.039 | Split_Wall_Mounted Samsung 1.5TR SEER 8.039 | Split_Wall_Mounted LG 1.46TR SEER 9.8
1229 | Split_Wall_Mounted | Carrier | 42XP100H3PE | Non-Inverter | 2.5 | 2.75 | 33000 | 3309.9298 | 9.97 | 29500 | 4057.7717 | 7.27 | 8.54 | Split_Wall_Mounted Carrier 2.75TR SEER 8.54 | Split_Wall_Mounted Carrier 2.75TR SEER 8.54
1230 | Split_Wall_Mounted | LG | S242MH ST0 | Non-Inverter | 2 | 1.91 | 22996.8723 | 2630 | 8.74 | 20062.5533 | 3035 | 6.6104 | 7.54 | Split_Wall_Mounted LG 1.91TR SEER 7.54 | Split_Wall_Mounted LG 1.91TR SEER 7.54
1231 | Split_Wall_Mounted | LG | NS242H3 | Inverter | 1.5 | 1.79 | 21500 | 1734 | 12.39 | 18500 | 2127 | 8.6977 | 10.47 | Split_Wall_Mounted LG 1.79TR SEER 10.47 | Inverter unit "No replacement"
1232 | Split_Wall_Mounted | LG | NT382H | Inverter | 2.5 | 2.5 | 30000 | 2440 | 12.29 | 25400 | 2885 | 8.8042 | 10.43 | Split_Wall_Mounted LG 2.5TR SEER 10.43 | Inverter unit "No replacement"
1233 | Split_Wall_Mounted | Arven | ARS120FE6X | Non-Inverter | 1.5 | 1.53 | 18400 | 1510 | 12.18 | 15800 | 1800 | 8.7778 | 10.36 | Split_Wall_Mounted Arven 1.53TR SEER 10.36 | Split_Wall_Mounted Okia 1.53TR SEER 10.37
1234 | Split_Wall_Mounted | Haam | S-036H/hr | Non-Inverter | 2.5 | 2.5 | 30000 | 3460 | 8.67 | 25200 | 3900 | 6.4615 | 7.43 | Split_Wall_Mounted Haam 2.5TR SEER 7.43 | Split_Wall_Mounted Royal Temp 2.5TR SEER 7.53
1235 | Split_Wall_Mounted | Crown | CROWN24C | Non-Inverter | 2 | 1.79 | 21500 | 1770 | 12.14 | 18600 | 2130 | 8.7324 | 10.33 | Split_Wall_Mounted Crown 1.79TR SEER 10.33 | Split_Wall_Mounted Crown 1.79TR SEER 10.33
1236 | Split_Wall_Mounted | Kimatsu | KSA 30000 CH | Non-Inverter | 2 | 2.03 | 24450 | 2054 | 11.9 | 20950 | 2464 | 8.5024 | 10.1 | Split_Wall_Mounted Kimatsu 2.03TR SEER 10.1 | Split_Wall_Mounted GREE 2.19TR SEER 10.05
1237 | Split_Wall_Mounted | Haam | HM24CWM | Non-Inverter | 2 | 1.9 | 22800 | 1880 | 12.12 | 19220 | 2210 | 8.6968 | 10.29 | Split_Wall_Mounted Haam 1.9TR SEER 10.29 | Split_Wall_Mounted Mando 1.84TR SEER 10.28
1238 | Split_Wall_Mounted | Lakes | LSAC-24C/A | Non-Inverter | 1.5 | 1.73 | 20813 | 2420 | 8.6 | 17742 | 2650 | 6.6951 | 7.46 | Split_Wall_Mounted Lakes 1.73TR SEER 7.46 | Split_Wall_Mounted Daikin 1.78TR SEER 7.47
1239 | Split_Wall_Mounted | Unix | MUNIXSP-12CN | Non-Inverter | 1 | 1 | 12000 | 1020 | 11.76 | 10500 | 1230 | 8.5366 | 10.04 | Split_Wall_Mounted Unix 1TR SEER 10.04 | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
1240 | Split_Wall_Mounted | Falcon | FSEH 19K5 | Non-Inverter | 1.5 | 1.55 | 18600 | 2450 | 7.59 | 14780.7791 | 2830 | 5.2229 | 6.34 | Split_Wall_Mounted Falcon 1.55TR SEER 6.34 | Split_Wall_Mounted LG 1.41TR SEER 6.94
1241 | Split_Wall_Mounted | Mando | AC-MD18H-FW | Non-Inverter | 1.5 | 1.43 | 17197 | 1431 | 12.01 | 14899 | 1703 | 8.7487 | 10.26 | Split_Wall_Mounted Mando 1.43TR SEER 10.26 | Split_Wall_Mounted Cooline 1.5TR SEER 10.25
1242 | Split_Wall_Mounted | LG | S3228Q | Non-Inverter | 2 | 2.21 | 26613.5911 | 2790 | 9.53 | 23713.3921 | 3450 | 6.8734 | 8.13 | Split_Wall_Mounted LG 2.21TR SEER 8.13 | Split_Wall_Mounted LG 2.21TR SEER 8.14
1243 | Split_Wall_Mounted | LG | S182NH / GS-H1825NB2 | Non-Inverter | 1.5 | 1.49 | 17981.234 | 2060 | 8.72 | 15490.4748 | 2370 | 6.5361 | 7.5 | Split_Wall_Mounted LG 1.49TR SEER 7.5 | Split_Wall_Mounted LG 1.46TR SEER 7.56
1244 | Split_Wall_Mounted | Haam | HM18H/7S16 | Non-Inverter | 1.5 | 1.45 | 17400 | 1510 | 11.52 | 14900 | 1730 | 8.6127 | 9.89 | Split_Wall_Mounted Haam 1.45TR SEER 9.89 | Split_Wall_Mounted Chigo 1.38TR SEER 9.88
1245 | Split_Wall_Mounted | Samsung | ARS24HPFNBWKN | Non-Inverter | 2 | 1.93 | 23200 | 2340 | 9.91 | 20230 | 2700 | 7.4926 | 8.55 | Split_Wall_Mounted Samsung 1.93TR SEER 8.55 | Split_Wall_Mounted Carrier 2TR SEER 8.60
1246 | Split_Wall_Mounted | Starway | SWAC24KC | Non-Inverter | 2 | 1.84 | 22100 | 1811 | 12.2 | 18400 | 2152 | 8.5502 | 10.27 | Split_Wall_Mounted Starway 1.84TR SEER 10.27 | Split_Wall_Mounted Mando 1.84TR SEER 10.28
1247 | Split_Wall_Mounted | Awalgulf | EWAA18SC2BCBX | Non-Inverter | 1.5 | 1.43 | 17200 | 1490 | 11.54 | 15239 | 1836 | 8.3001 | 9.83 | Split_Wall_Mounted Awalgulf 1.43TR SEER 9.83 | Split_Wall_Mounted LG 1.45TR SEER 9.84
1248 | Split_Wall_Mounted | Zamil | MH180CEB | Non-Inverter | 1.5 | 1.5 | 18000 | 2200 | 8.18 | 12800 | 2400 | 5.3333 | 6.69 | Split_Wall_Mounted Zamil 1.5TR SEER 6.69 | Split_Wall_Mounted LG 1.41TR SEER 6.94
1249 | Split_Wall_Mounted | General | EASN36H1 | Non-Inverter | 2.5 | 2.41 | 29012 | 2454 | 11.82 | 24720 | 2944 | 8.3967 | 10.01 | Split_Wall_Mounted General 2.41TR SEER 10.01 | Split_Wall_Mounted Royal Temp 2.5TR SEER 7.53
1250 | Split_Wall_Mounted | General | EASN24H2 | Non-Inverter | 1.5 | 1.75 | 21040 | 1815 | 11.59 | 17060 | 2055 | 8.3017 | 9.8 | Split_Wall_Mounted General 1.75TR SEER 9.8 | Split_Wall_Mounted LG 1.82TR SEER 9.79
1251 | Split_Wall_Mounted | Crown | BSACL-F12C7 | Non-Inverter | 1 | 0.93 | 11260 | 930 | 12.1 | 9895 | 1150 | 8.6043 | 10.28 | Split_Wall_Mounted Crown 0.93TR SEER 10.28 | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
1252 | Split_Wall_Mounted | Zamil | ADX18ECAXFQ | Non-Inverter | 1.5 | 1.49 | 17994 | 2250 | 7.99 | 14995 | 2500 | 5.998 | 6.86 | Split_Wall_Mounted Zamil 1.49TR SEER 6.86 | Split_Wall_Mounted LG 1.41TR SEER 6.94
1253 | Split_Wall_Mounted | Zamil | AHM18CEBW | Non-Inverter | 1.5 | 1.5 | 18000 | 2100 | 8.57 | 15000 | 2400 | 6.25 | 7.29 | Split_Wall_Mounted Zamil 1.5TR SEER 7.29 | Split_Wall_Mounted LG 1.46TR SEER 7.28
1254 | Split_Wall_Mounted | Gree | GWC18MC-D1TA3A/O | Non-Inverter | 1.5 | 1.5 | 18083 | 2250 | 8.03 | 16200 | 2550 | 6.3529 | 7.03 | Split_Wall_Mounted Gree 1.5TR SEER 7.03 | Split_Wall_Mounted Gree 1.5TR SEER 7.03
1255 | Split_Wall_Mounted | Fuji | RSA30RBT | Non-Inverter | 2 | 2.16 | 26000 | 3210 | 8.09 | 22900 | 3600 | 6.3611 | 7.06 | Split_Wall_Mounted Fuji 2.16TR SEER 7.06 | Split_Wall_Mounted MITSUBISHI 2.03TR SEER 7.10
1256 | Split_Wall_Mounted | Mando | MP920-24H | Non-Inverter | 2 | 1.83 | 22000 | 1781 | 12.35 | 18400 | 2114 | 8.7039 | 10.42 | Split_Wall_Mounted Mando 1.83TR SEER 10.42 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
1257 | Split_Wall_Mounted | Arrow | RO-12LHX | Non-Inverter | 1 | 0.93 | 11260 | 930 | 12.1 | 9895 | 1150 | 8.6043 | 10.28 | Split_Wall_Mounted Arrow 0.93TR SEER 10.28 | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
1258 | Split_Wall_Mounted | Starway | SWT18HR | Non-Inverter | 1.5 | 1.51 | 18185.98 | 1840 | 9.88 | 15285.76 | 2100 | 7.2789 | 8.44 | Split_Wall_Mounted Starway 1.51TR SEER 8.44 | Split_Wall_Mounted LG 1.5TR SEER 8.40
1259 | Split_Wall_Mounted | Ugine | UTS24LSHR-7 | Non-Inverter | 2 | 1.87 | 22500 | 1899 | 11.84 | 19000 | 2235 | 8.5011 | 10.05 | Split_Wall_Mounted Ugine 1.87TR SEER 10.05 | Split_Wall_Mounted Carrier 1.83TR SEER 10.08
1260 | Split_Wall_Mounted | Ugine | UTS30LSHC-7 | Non-Inverter | 2 | 2.19 | 26300 | 2230 | 11.79 | 22800 | 2680 | 8.5075 | 10.04 | Split_Wall_Mounted Ugine 2.19TR SEER 10.04 | Split_Wall_Mounted GREE 2.19TR SEER 10.05
1261 | Split_Wall_Mounted | Ugine | UTS36LSHC-7 | Non-Inverter | 2.5 | 2.5 | 30000 | 2540 | 11.81 | 25200 | 2960 | 8.5135 | 10.032 | Split_Wall_Mounted Ugine 2.5TR SEER 10.032 | Split_Wall_Mounted LG 2.5TR SEER 10.43
1262 | Split_Wall_Mounted | MAU | MAUSP-24CN | Non-Inverter | 2 | 1.9 | 22800 | 1880 | 12.12 | 19220 | 2210 | 8.6968 | 10.29 | Split_Wall_Mounted MAU 1.9TR SEER 10.29 | Split_Wall_Mounted Mando 1.84TR SEER 10.28
1263 | Split_Wall_Mounted | HI Home | HSO24HC-7 | Non-Inverter | 2 | 1.87 | 22500 | 1899 | 11.84 | 19000 | 2235 | 8.5011 | 10.05 | Split_Wall_Mounted HI Home 1.87TR SEER 10.05 | Split_Wall_Mounted Carrier 1.83TR SEER 10.08
1264 | Split_Wall_Mounted | Samsung | AR24MRFHRWKN | Non-Inverter | 1.5 | 1.66 | 20000 | 1690 | 11.83 | 18500 | 1950 | 9.4872 | 10.42 | Split_Wall_Mounted Samsung 1.66TR SEER 10.42 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
1265 | Split_Wall_Mounted | Comfort | MSAC-18CHS/XT7 | Non-Inverter | 1.5 | 1.5 | 18000 | 1524 | 11.81 | 15500 | 1810 | 8.5635 | 10.067 | Split_Wall_Mounted Comfort 1.5TR SEER 10.067 | Split_Wall_Mounted LG 1.47TR SEER 10.15
1266 | Split_Wall_Mounted | Samsung | AS24UUPN | Non-Inverter | 2 | 2 | 24000 | 2750 | 8.72 | 19828.35 | 3200 | 6.1964 | 7.37 | Split_Wall_Mounted Samsung 2TR SEER 7.37 | Split_Wall_Mounted Zamil 2.11TR SEER7.24
1267 | Split_Wall_Mounted | Samsung | AQ18UUQN | Non-Inverter | 1.5 | 1.5 | 18000 | 1900 | 9.47 | 15278 | 2250 | 6.7902 | 8.04 | Split_Wall_Mounted Samsung 1.5TR SEER 8.04 | Split_Wall_Mounted LG 1.54TR SEER 8.14
1268 | Split_Wall_Mounted | Samsung | AQ18UUQX | Non-Inverter | 1.5 | 1.5 | 18000 | 1900 | 9.47 | 15267.8295 | 2250 | 6.7857 | 8.03 | Split_Wall_Mounted Samsung 1.5TR SEER 8.03 | Split_Wall_Mounted LG 1.54TR SEER 8.14
1269 | Split_Wall_Mounted | Chigo | CSA-18CO | Non-Inverter | 1.5 | 1.45 | 17400 | 1810 | 9.61 | 15300 | 2100 | 7.2857 | 8.3 | Split_Wall_Mounted Chigo 1.45TR SEER 8.3 | Split_Wall_Mounted LG 1.53TR SEER 8.30
1270 | Split_Wall_Mounted | Chigo | CZS-18CO | Non-Inverter | 1.5 | 1.38 | 16675 | 1450 | 11.5 | 14362 | 1670 | 8.6 | 9.88 | Split_Wall_Mounted Chigo 1.38TR SEER 9.88 | Split_Wall_Mounted Chigo 1.38TR SEER 9.88
1271 | Split_Wall_Mounted | Chigo | CZS-12CO | Non-Inverter | 1 | 0.98 | 11845 | 1030 | 11.5 | 10164 | 1210 | 8.4 | 9.81 | Split_Wall_Mounted Chigo 0.98TR SEER 9.81 | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
1272 | Split_Wall_Mounted | Haam | HM24H/7S17 | Non-Inverter | 1.5 | 1.62 | 19550 | 1700 | 11.5 | 17264 | 2080 | 8.3 | 9.81 | Split_Wall_Mounted Haam 1.62TR SEER 9.81 | Split_Wall_Mounted Zamil 1.47TR SEER 9.8
1273 | Split_Wall_Mounted | Gree | GWC18ACD-D3NTA1G/O | Non-Inverter | 1.5 | 1.5 | 18000 | 1481 | 12.15 | 15000 | 1754 | 8.5519 | 10.25 | Split_Wall_Mounted Gree 1.5TR SEER 10.25 | Split_Wall_Mounted Cooline 1.5TR SEER 10.25
1274 | Split_Wall_Mounted | MTC | MTC12CT19N | Non-Inverter | 1 | 1 | 12100 | 1021 | 11.85 | 10600 | 1269 | 8.353 | 10.03 | Split_Wall_Mounted MTC 1TR SEER 10.03 | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
1275 | Split_Wall_Mounted | Gree | HSL24RHN1-SA | Non-Inverter | 1.5 | 1.75 | 21000 | 1729 | 12.14 | 17500 | 2047 | 8.5491 | 10.24 | Split_Wall_Mounted Gree 1.75TR SEER 10.24 | Split_Wall_Mounted LG 1.83TR SEER 10.27
1276 | Split_Wall_Mounted | Dansat | DSH24CH | Non-Inverter | 2 | 1.83 | 22000 | 1850 | 11.89 | 19500 | 2250 | 8.6667 | 10.17 | Split_Wall_Mounted Dansat 1.83TR SEER 10.17 | Split_Wall_Mounted Gree 1.83TR SEER 10.17
1277 | Split_Wall_Mounted | Mando | AC-24H-MP | Non-Inverter | 2 | 1.93 | 23202 | 2000 | 11.6 | 19899 | 2390 | 8.3259 | 9.85 | Split_Wall_Mounted Mando 1.93TR SEER 9.85 | Split_Wall_Mounted LG 1.74TR SEER 9.84
1278 | Split_Wall_Mounted | Sky star | SKYSTAR-24CH | Non-Inverter | 2 | 1.84 | 22178 | 1820 | 12.18 | 19107 | 2200 | 8.685 | 10.34 | Split_Wall_Mounted Sky star 1.84TR SEER 10.34 | Split_Wall_Mounted Crown 1.79TR SEER 10.33
1279 | Split_Wall_Mounted | Unistar | UNISTARS-24C | Non-Inverter | 1.5 | 1.79 | 21580.9 | 2200 | 9.8 | 19790.6 | 2530 | 7.8224 | 8.62 | Split_Wall_Mounted Unistar 1.79TR SEER 8.62 | Split_Wall_Mounted Carrier 1.79TR SEER 8.31
1280 | Split_Wall_Mounted | General | GS TN12C | Non-Inverter | 1 | 0.95 | 11500 | 930 | 12.36 | 9900 | 1135 | 8.7225 | 10.46 | Split_Wall_Mounted General 0.95TR SEER 10.46 | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
1281 | Split_Wall_Mounted | Daewoo | DSA-240L-R | Non-Inverter | 2 | 2 | 24000 | 2500 | 9.6 | 17500 | 2850 | 6.1404 | 7.82 | Split_Wall_Mounted Daewoo 2TR SEER 7.82 | Split_Wall_Mounted DAEWOO 2TR SEER 7.86
1282 | Split_Wall_Mounted | General Electric | GESFAC18INT | Non-Inverter | 1.5 | 1.5 | 18000 | 1481 | 12.15 | 15300 | 1789 | 8.5523 | 10.27 | Split_Wall_Mounted General Electric 1.5TR SEER 10.27 | Split_Wall_Mounted Cooline 1.5TR SEER 10.25
1283 | Split_Wall_Mounted | York | YJFE24XH3CHA-R4 | Non-Inverter | 2 | 1.83 | 22000 | 1811 | 12.14 | 19000 | 2222 | 8.5509 | 10.27 | Split_Wall_Mounted York 1.83TR SEER 10.27 | Split_Wall_Mounted LG 1.83TR SEER 10.27
1284 | Split_Wall_Mounted | Haas | HSA125FE6H | Non-Inverter | 2 | 1.91 | 23000 | 1870 | 12.29 | 19800 | 2275 | 8.7033 | 10.42 | Split_Wall_Mounted Haas 1.91TR SEER 10.42 | Split_Wall_Mounted Mando 1.84TR SEER 10.28
1285 | Split_Wall_Mounted | York | YQFE24XH3CHPR5 | Non-Inverter | 2 | 1.83 | 22000 | 1810 | 12.15 | 19000 | 2222 | 8.5509 | 10.28 | Split_Wall_Mounted York 1.83TR SEER 10.28 | Split_Wall_Mounted LG 1.83TR SEER 10.27
1286 | Split_Wall_Mounted | York | YQFE30XH3CHQ-R5 | Non-Inverter | 2.5 | 2.28 | 27400 | 2283 | 12 | 23200 | 2682 | 8.6503 | 10.2 | Split_Wall_Mounted York 2.28TR SEER 10.2 | Split_Wall_Mounted LG 2.5TR SEER 10.43
1287 | Split_Wall_Mounted | Gree | GWC24MD-D1NTA8GI | Non-Inverter | 2 | 1.83 | 22000 | 2234 | 9.84 | 19600 | 2741 | 7.1507 | 8.42 | Split_Wall_Mounted Gree 1.83TR SEER 8.42 | Split_Wall_Mounted LG 1.82TR SEER 9.79
1288 | Split_Wall_Mounted | Zamil | ADO26CHXOW | Non-Inverter | 2 | 1.99 | 23998 | 2078 | 11.54 | 19299 | 2325 | 8.3006 | 9.77 | Split_Wall_Mounted Zamil 1.99TR SEER 9.77 | Split_Wall_Mounted Zamil 1.99TR SEER9.77
1289 | Split_Wall_Mounted | SkyStar | ARTI030CV60N0FR | Non-Inverter | 2.5 | 2.33 | 28000 | 2393 | 11.7 | 23500 | 2828 | 8.3098 | 9.9 | Split_Wall_Mounted SkyStar 2.33TR SEER 9.9 | Split_Wall_Mounted Zamil 2.35TR SEER 9.85
1290 | Split_Wall_Mounted | Hisense | AS-30HTS | Non-Inverter | 2.5 | 2.27 | 27300 | 2255 | 12.1 | 24200 | 2775 | 8.7207 | 10.33 | Split_Wall_Mounted Hisense 2.27TR SEER 10.33 | Split_Wall_Mounted Zamil 2.24TR SEER 10.35
1291 | Split_Wall_Mounted | Frego | AXI12CV60L0FR | Non-Inverter | 1 | 0.95 | 11400 | 974 | 11.7 | 9300 | 1120 | 8.3036 | 9.88 | Split_Wall_Mounted Frego 0.95TR SEER 9.88 | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
1292 | Split_Floor_Standing | Basic | BVSACL-F60H7BVSACL-C60H7 | Non-Inverter | 4.5 | 4.42 | 53040 | 4420 | 12 | 46198 | 5230 | 8.8333 | 10.28 | Split_Floor_Standing Basic 4.42TR SEER 10.28 | Split_Floor_Standing Samsung 4TR SEER 10.3
1293 | Split_Floor_Standing | SkyStar | EQB60SCAC2 | Non-Inverter | 4.5 | 4.55 | 54600 | 4731 | 11.54 | 46956 | 5651 | 8.3093 | 9.82 | Split_Floor_Standing SkyStar 4.55TR SEER 9.82 | Split_Floor_Standing Zamil 4.421TR SEER 10.15
1294 | Split_Floor_Standing | Frego | FF50X2M7 | Non-Inverter | 4 | 3.85 | 46200 | 3970 | 11.63 | 41000 | 4920 | 8.3333 | 9.91 | Split_Floor_Standing Frego 3.85TR SEER 9.91 | Split_Floor_Standing Carrier 4TR SEER 9.95
1295 | Split_Floor_Standing | Frego | FF60X2H | Non-Inverter | 4 | 3.95 | 47400 | 3890 | 12.18 | 40800 | 4740 | 8.6076 | 10.31 | Split_Floor_Standing Frego 3.95TR SEER 10.31 | Split_Floor_Standing Samsung 4TR SEER 10.3
1296 | Split_Wall_Mounted | Frego | FW18X-2A7 | Non-Inverter | 1.5 | 1.5 | 18000 | 1525 | 11.8 | 14900 | 1773 | 8.4038 | 9.98 | Split_Wall_Mounted Frego 1.5TR SEER 9.98 | Split_Wall_Mounted GREE 1.5TR SEER 9.98
1297 | Split_Wall_Mounted | Frego | FW24C-2Q9 | Non-Inverter | 2 | 1.8 | 21600 | 1800 | 12 | 18400 | 2200 | 8.3636 | 10.11 | Split_Wall_Mounted Frego 1.8TR SEER 10.11 | Split_Wall_Mounted Carrier 1.83TR SEER 10.08
1298 | Split_Wall_Mounted | Frego | FW30C-2Q9 | Non-Inverter | 2 | 2.13 | 25600 | 2100 | 12.19 | 21700 | 2550 | 8.5098 | 10.27 | Split_Wall_Mounted Frego 2.13TR SEER 10.27 | Split_Wall_Mounted Carrier 2.25TR SEER 10.20
1299 | Split_Wall_Mounted | Frego | FW30X-2T7 | Non-Inverter | 2 | 2.04 | 24500 | 2110 | 11.61 | 19790 | 2385 | 8.2977 | 9.81 | Split_Wall_Mounted Frego 2.04TR SEER 9.81 | Split_Wall_Mounted LG 1.99TR SEER 9.80
1300 | Split_Wall_Mounted | Frego | FW30Y2S7 | Non-Inverter | 2.5 | 2.31 | 27800 | 2310 | 12.03 | 24200 | 2740 | 8.8321 | 10.3 | Split_Wall_Mounted Frego 2.31TR SEER 10.3 | Split_Wall_Mounted Zamil 2.24TR SEER 10.35
1301 | Split_Wall_Mounted | Zamil | MAZ12CHXAW | Non-Inverter | 1 | 0.91 | 11000 | 1010 | 10.89 | 10100 | 1210 | 8.3471 | 9.47 | Split_Wall_Mounted Zamil 0.91TR SEER 9.47 | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
1302 | Split_Wall_Mounted | HITACHI | RAC-19JHP4 | Non-Inverter | 1.5 | 1.38 | 16620 | 1820 | 9.13 | 15870 | 2140 | 7.4159 | 8.09 | Split_Wall_Mounted HITACHI 1.38TR SEER 8.09 | Split_Wall_Mounted LG 1.52TR SEER 8.15
1303 | Split_Wall_Mounted | Kleenair | S12CSA | Non-Inverter | 1 | 0.97 | 11700 | 1008 | 11.6 | 10080 | 1215 | 8.2963 | 9.86 | Split_Wall_Mounted Kleenair 0.97TR SEER 9.86 | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
1304 | Split_Wall_Mounted | SkyStar | SKYSTAR-24UB | Non-Inverter | 2 | 1.8 | 21600 | 1800 | 12 | 18400 | 2200 | 8.3636 | 10.11 | Split_Wall_Mounted SkyStar 1.8TR SEER 10.11 | Split_Wall_Mounted Carrier 1.83TR SEER 10.08
1305 | Split_Wall_Mounted | SkyStar | SKYSTAR-30UB | Non-Inverter | 2 | 2.13 | 25600 | 2100 | 12.19 | 21700 | 2550 | 8.5098 | 10.27 | Split_Wall_Mounted SkyStar 2.13TR SEER 10.27 | Split_Wall_Mounted Carrier 2.25TR SEER 10.20
1306 | Split_Wall_Mounted | LG | S252SH | Non-Inverter | 2 | 2.08 | 25000 | 2750 | 9.09 | 20813.2 | 3000 | 6.9377 | 7.83 | Split_Wall_Mounted LG 2.08TR SEER 7.83 | Split_Wall_Mounted DAEWOO 2TR SEER 7.86
1307 | Split_Wall_Mounted | Carrier | 40FWD030-303DA | Non-Inverter | 2.5 | 2.5 | 30000 | 3086.4198 | 9.72 |  |  |  | - | Split_Wall_Mounted Carrier 2.5TR SEER - | Split_Wall_Mounted LG 2.58TR SEER 9.72
1308 | Split_Wall_Mounted | Panorama | PWC30M1T | Non-Inverter | 2.5 | 2.33 | 28000 | [5 empty] | - | Split_Wall_Mounted Panorama 2.33TR SEER - | Split_Wall_Mounted Zamil 2.11TR SEER7.24
1309 | Split_Wall_Mounted | Panorama | PWH18M6I | Non-Inverter | 1.5 | 1.48 | 17800 | [5 empty] | - | Split_Wall_Mounted Panorama 1.48TR SEER - | Split_Wall_Mounted LG 1.41TR SEER 6.94
1310 | Split_Wall_Mounted | Luna | LAC-240CAU | Non-Inverter | 2 | 1.8 | 21600 | 1800 | 12 | 18400 | 2200 | 8.3636 | 10.11 | Split_Wall_Mounted Luna 1.8TR SEER 10.11 | Split_Wall_Mounted Carrier 1.83TR SEER 10.08
1311 | Split_Wall_Mounted | Gree | GWC30FA-D1NTA3B/I | Non-Inverter | 2 | 2.27 | 27300 | [5 empty] | - | Split_Wall_Mounted Gree 2.27TR SEER - | Split_Wall_Mounted Zamil 2.11TR SEER7.24
1312 | Split_Wall_Mounted | Alessa | DS24FE6GP3 | Non-Inverter | 2 | 1.9 | 22833 | [5 empty] | - | Split_Wall_Mounted Alessa 1.9TR SEER - | Split_Wall_Mounted Zamil 2TR SEER 6.69
1313 | Split_Wall_Mounted | Akai | AK25WSC | Non-Inverter | 2 | 1.8 | 21666.2 | 3500 | 6.19 |  |  |  | - | Split_Wall_Mounted Akai 1.8TR SEER - | Split_Wall_Mounted Zamil 2TR SEER 6.69
1314 | Split_Wall_Mounted | Akai | GH12C | Non-Inverter | 1 | 0.9 | 10800 | 1250 | 8.64 | 8208 | 1440 | 5.7 | 7.12 | Split_Wall_Mounted Akai 0.9TR SEER 7.12 | Split_Wall_Mounted LG 0.95TR SEER 7.9
1315 | Split_Floor_Standing | Arrow | RO-60CLA-H | Non-Inverter | 4 | 3.95 | 47400 | 3890 | 12.18 | 40800 | 4740 | 8.6076 | 10.31 | Split_Floor_Standing Arrow 3.95TR SEER 10.31 | Split_Floor_Standing Samsung 4TR SEER 10.3
1316 | Split_Wall_Mounted | Arrow | RO-18CBA-C | Non-Inverter | 1.5 | 1.44 | 17300 | 1430 | 12.09 | 14900 | 1710 | 8.7135 | 10.29 | Split_Wall_Mounted Arrow 1.44TR SEER 10.29 | Split_Wall_Mounted Cooline 1.5TR SEER 10.25
1317 | Split_Wall_Mounted | AUX | AUX 24CN | Inverter | 2 | 1.8 | 21600 | 1800 | 12 | 18400 | 2200 | 8.3636 | 10.11 | Split_Wall_Mounted AUX 1.8TR SEER 10.11 | Inverter unit "No replacement"
1318 | Split_Wall_Mounted | AUX | AUX 24CF | Non-Inverter | 2 | 1.79 | 21495 | 1800 | 11.94 | 18425 | 2150 | 8.5698 | 10.15 | Split_Wall_Mounted AUX 1.79TR SEER 10.15 | Split_Wall_Mounted Carrier 1.84TR SEER 10.16
1319 | Split_Wall_Mounted | AUX | AUX 18C | Non-Inverter | 1.5 | 1.49 | 17913 | 1480.4132 | 12.1 | 15354 | 1760 | 8.7239 | 10.29 | Split_Wall_Mounted AUX 1.49TR SEER 10.29 | Split_Wall_Mounted Cooline 1.5TR SEER 10.25
1320 | Split_Wall_Mounted | BANCOOL | AMBC24DC | Inverter | 2 | 1.81 | 21800 | 1816.6667 | 12 | 18400 | 2206.235 | 8.34 | 10.1 | Split_Wall_Mounted BANCOOL 1.81TR SEER 10.1 | Inverter unit "No replacement"
1321 | Split_Wall_Mounted | Basic | BSAC-F24CS | Non-Inverter | 2 | 1.76 | 21154 | [5 empty] | - | Split_Wall_Mounted Basic 1.76TR SEER - | Split_Wall_Mounted LG 1.87TR SEER 7.14
1322 | Split_Wall_Mounted | Basic | BSACCA-F130CB | Inverter | 2 | 2.28 | 27400 | 2220 | 12.34 | 24800 | 2950 | 8.4068 | 10.38 | Split_Wall_Mounted Basic 2.28TR SEER 10.38 | Inverter unit "No replacement"
1323 | Split_Wall_Mounted | Basic | BSAC-24C5 | Non-Inverter | 2 | 1.83 | 22000 | 2260 | 9.73 | 19000 | 2675 | 7.1028 | 8.31 | Split_Wall_Mounted Basic 1.83TR SEER 8.31 | Split_Wall_Mounted Carrier 1.79TR SEER 8.31
1324 | Split_Wall_Mounted | Basic | BSAC-F36H5 | Non-Inverter | 2.5 | 2.66 | 32004 | 3257 | 9.82 | 29991 | 3995 | 7.5071 | 8.56 | Split_Wall_Mounted Basic 2.66TR SEER 8.56 | Split_Wall_Mounted Carrier 2.75TR SEER 8.54
1325 | Split_Wall_Mounted | Basic | BSACH-F18CD | Non-Inverter | 1.5 | 1.48 | 17813 | 1480 | 12.03 | 15354 | 1780 | 8.6258 | 10.23 | Split_Wall_Mounted Basic 1.48TR SEER 10.23 | Split_Wall_Mounted Ugine 1.48TR SEER 10.23
1326 | Split_Wall_Mounted | Basic | BSSL186CAU | Non-Inverter | 1.5 | 1.49 | 17913 | 1480 | 12.1 | 15354 | 1760 | 8.7239 | 10.3 | Split_Wall_Mounted Basic 1.49TR SEER 10.3 | Split_Wall_Mounted Mando 1.5TR SEER 10.35
1327 | Split_Wall_Mounted | Besat | BSSL246CAU | Non-Inverter | 2 | 1.84 | 22178 | 1820 | 12.18 | 19107 | 2200 | 8.685 | 10.34 | Split_Wall_Mounted Besat 1.84TR SEER 10.34 | Split_Wall_Mounted Crown 1.79TR SEER 10.33
1328 | Split_Floor_Standing | Carrier | 42SFL7B1A | Non-Inverter | 4.5 | 4.66 | 56000 | 4590 | 12.2 | 50000 | 5556 | 8.9993 | 10.48 | Split_Floor_Standing Carrier 4.66TR SEER 10.48 | Split_Floor_Standing Zamil 4.421TR SEER 10.15
1329 | Split_Wall_Mounted | Champion | CHSAI-18H | Non-Inverter | 1.5 | 1.5 | 18000 | 1940 | 9.27 | 16100 | 2370 | 6.7932 | 7.95 | Split_Wall_Mounted Champion 1.5TR SEER 7.95 | Split_Wall_Mounted LG 1.54TR SEER 8.14
1330 | Split_Wall_Mounted | CHIGO | CSA-30CO | Non-Inverter | 2 | 1.99 | 23884 | 2670 | 8.94 | 21836.8 | 3100 | 7.0441 | 7.83 | Split_Wall_Mounted CHIGO 1.99TR SEER 7.83 | Split_Wall_Mounted DAEWOO 2TR SEER 7.86
1331 | Split_Wall_Mounted | Class | CL24E6 | Non-Inverter | 2 | 1.7 | 20472 | 3200 | 6.39 | 23500 | 2600 | 9.0385 | 6.56 | Split_Wall_Mounted Class 1.7TR SEER 6.56 | Split_Wall_Mounted LG 1.74TR SEER 8.20
1332 | Split_Wall_Mounted | Class | CL18E6 | Non-Inverter | 1.5 | 1.5 | 18000 | 2040 | 8.82 |  |  |  | - | Split_Wall_Mounted Class 1.5TR SEER - | Split_Wall_Mounted LG 1.5TR SEER 8.40
1333 | Split_Wall_Mounted | Class | CL24E6XL | Non-Inverter | 2 | 1.84 | 22178 | 1820 | 12.18 | 19107 | 2200 | 8.685 | 10.34 | Split_Wall_Mounted Class 1.84TR SEER 10.34 | Split_Wall_Mounted Crown 1.79TR SEER 10.33
1334 | Split_Wall_Mounted | Classic | ADU24CHAXFQ | Non-Inverter | 2 | 1.95 | 23491.62 | 2975 | 7.89 | 18994.604 | 3325 | 5.7127 | 6.69 | Split_Wall_Mounted Classic 1.95TR SEER 6.69 | Split_Wall_Mounted Zamil 2TR SEER 6.69
1335 | Split_Wall_Mounted | ultra Plus | HWX30ECAYFU | Non-Inverter | 2.5 | 2.41 | 29000 | 3100 | 9.35 |  |  |  | - | Split_Wall_Mounted ultra Plus 2.41TR SEER - | Split_Wall_Mounted LG 2.58TR SEER 9.72
1336 | Split_Floor_Standing | Comfort line | MSAC-48CF7 | Non-Inverter | 4 | 3.69 | 44356 | 3845 | 11.53 |  |  |  | - | Split_Floor_Standing Comfort line 3.69TR SEER - | Split_Floor_Standing LG 4TR SEER 10.51
1337 | Split_Wall_Mounted | Comfort line | MSAC-12CHS/GT2 | Non-Inverter | 1 | 0.89 | 10768.272 | 1299 | 8.28 |  |  |  | - | Split_Wall_Mounted Comfort line 0.89TR SEER - | Split_Wall_Mounted LG 0.95TR SEER 8.3
1338 | Split_Wall_Mounted | Comfort line | MSAC-18CS/P2 | Non-Inverter | 1.5 | 1.53 | 18400 | 1484 | 12.39 | 15300 | 1800 | 8.5 | 10.38 | Split_Wall_Mounted Comfort line 1.53TR SEER 10.38 | Split_Wall_Mounted Mando 1.53TR SEER 10.38
1339 | Split_Wall_Mounted | Comfort line | MSAC-30CS/P1 | Non-Inverter | 2.5 | 2.3 | 27600 | 2262 | 12.2 | 23300 | 2670 | 8.7266 | 10.35 | Split_Wall_Mounted Comfort line 2.3TR SEER 10.35 | Split_Wall_Mounted Zamil 2.24TR SEER 10.35
1340 | Split_Wall_Mounted | Cooline | TAL24CCXED | Non-Inverter | 2 | 1.75 | 21100 | 1744 | 12.09 |  |  |  | - | Split_Wall_Mounted Cooline 1.75TR SEER - | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
1341 | Split_Wall_Mounted | Craft | DSA36FE6YHA1 | Non-Inverter | 2.5 | 2.6 | 31200 | 2580 | 12.09 | 27200 | 3145 | 8.6486 | 10.28 | Split_Wall_Mounted Craft 2.6TR SEER 10.28 | Split_Wall_Mounted Carrier 2.58TR SEER 10.41
1342 | Split_Wall_Mounted | Craft | DS24FE7M5 | Non-Inverter | 2 | 2.01 | 24200 | 2530 | 9.56 | 20001.144 | 2850 | 7.0179 | 8.15 | Split_Wall_Mounted Craft 2.01TR SEER 8.15 | Split_Wall_Mounted LG 2.21TR SEER 8.14
1343 | Split_Wall_Mounted | Craft | 0524FE7M1 | Non-Inverter | 2 | 1.75 | 21000 | 1721 | 12.2 |  |  |  | - | Split_Wall_Mounted Craft 1.75TR SEER - | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
1344 | Split_Wall_Mounted | Alessa | DS24FE6GP3. | Non-Inverter | 2 | 1.9 | 22833 | [5 empty] | - | Split_Wall_Mounted Alessa 1.9TR SEER - | Split_Wall_Mounted Zamil 2TR SEER 6.69
1345 | Split_Wall_Mounted | Craft | DSA125FE6CL7 | Non-Inverter | 2 | 1.75 | 21000 | 1712 | 12.26 |  |  |  | - | Split_Wall_Mounted Craft 1.75TR SEER - | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
1346 | Split_Wall_Mounted | Craft | DSA25FE6GR7E | Non-Inverter | 2 | 1.83 | 22000 | [5 empty] | - | Split_Wall_Mounted Craft 1.83TR SEER - | Split_Wall_Mounted Zamil 2TR SEER 6.69
1347 | Split_Wall_Mounted | Craft | DSA30FE6GR7E | Non-Inverter | 2 | 2.27 | 27300 | [5 empty] | - | Split_Wall_Mounted Craft 2.27TR SEER - | Split_Wall_Mounted Zamil 2.11TR SEER7.24
1348 | Split_Floor_Standing | Craft | CF56FE7HS7FM | Non-Inverter | 4.5 | 4.3 | 51600 | 4250 | 12.14 | 44200 | 5250 | 8.419 | 10.22 | Split_Floor_Standing Craft 4.3TR SEER 10.22 | Split_Floor_Standing Zamil 4.421TR SEER 10.15
1349 | Split_Floor_Standing | Alessa | DS60FE7HS7FM | Non-Inverter | 4.5 | 4.39 | 52746 | 4404 | 11.97 | 45799.276 | 5454 | 8.3974 | 10.12 | Split_Floor_Standing Alessa 4.39TR SEER 10.12 | Split_Floor_Standing Zamil 4.421TR SEER 10.15
1350 | Split_Wall_Mounted | Craft | DSA25FE6GR7N | Non-Inverter | 2 | 1.83 | 22000 | [5 empty] | - | Split_Wall_Mounted Craft 1.83TR SEER - | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
1351 | Split_Wall_Mounted | Crony | CNY24CCF | Non-Inverter | 2 | 1.79 | 21495 | 1800 | 11.94 | 18425 | 2150 | 8.5698 | 10.15 | Split_Wall_Mounted Crony 1.79TR SEER 10.15 | Split_Wall_Mounted Carrier 1.84TR SEER 10.16
1352 | Split_Wall_Mounted | LG | GVSP24HC | Inverter | 2 | 1.83 | 22000 | 1795.9184 | 12.25 |  |  |  | - | Split_Wall_Mounted LG 1.83TR SEER - | Inverter unit "No replacement"
1353 | Split_Wall_Mounted | DAIYA | DA18CS | Non-Inverter | 1.5 | 1.5 | 18000 | [5 empty] | - | Split_Wall_Mounted DAIYA 1.5TR SEER - | Split_Wall_Mounted LG 1.41TR SEER 6.94
1354 | Split_Wall_Mounted | Dansat | DSA30WCH | Non-Inverter | 2 | 2.22 | 26700 | 2315 | 11.53 | 22500 | 2725 | 8.2569 | 9.78 | Split_Wall_Mounted Dansat 2.22TR SEER 9.78 | Split_Wall_Mounted Samsung 2.33TR SEER 9.83
1355 | Split_Wall_Mounted | CRONY | CRONY-24B2/SUA | Non-Inverter | 2 | 1.91 | 23001 | 2460 | 9.35 | 20003.2 | 3040 | 6.58 | 7.91 | Split_Wall_Mounted CRONY 1.91TR SEER 7.91 | Split_Wall_Mounted Carrier 1.81TR SEER 7.91
1356 | Split_Wall_Mounted | Eurostar | SA24C606S-T15 | Non-Inverter | 2 | 1.75 | 21040 | 1815 | 11.59 | 17060 | 2055 | 8.3017 | 9.8 | Split_Wall_Mounted Eurostar 1.75TR SEER 9.8 | Split_Wall_Mounted LG 1.82TR SEER 9.79
1357 | Split_Wall_Mounted | Falcon | FMS24CB | Inverter | 2 | 1.84 | 22100 | 1811 | 12.2 | 18400 | 2152 | 8.5502 | 10.28 | Split_Wall_Mounted Falcon 1.84TR SEER 10.28 | Inverter unit "No replacement"
1358 | Split_Wall_Mounted | NA | FLM24H | Non-Inverter | 2 | 1.84 | 22178 | 2437.1429 | 9.1 |  |  |  | - | Split_Wall_Mounted NA 1.84TR SEER - | Split_Wall_Mounted Carrier 2TR SEER 8.60
1359 | Split_Wall_Mounted | Falcon | FQS24C8 | Non-Inverter | 2 | 1.75 | 21000 | 1720 | 12.2 | 18000 | 2070 | 8.6957 | 10.35 | Split_Wall_Mounted Falcon 1.75TR SEER 10.35 | Split_Wall_Mounted Carrier 1.79TR SEER 10.35
1360 | Split_Wall_Mounted | Falcon | FTS30H | Non-Inverter | 2 | 2.2 | 26400 | 2129 | 12.4 |  |  |  | - | Split_Wall_Mounted Falcon 2.2TR SEER - | Split_Wall_Mounted Gree 2.25TR SEER 11.11
1361 | Split_Floor_Standing | Falcon | EQ048SCAA | Non-Inverter | 4 | 4 | 48000 | [5 empty] | - | Split_Floor_Standing Falcon 4TR SEER - | Split_Floor_Standing LG 4.35TR SEER 7.05
1362 | Split_Wall_Mounted | Falcon | FHS24H5 | Non-Inverter | 2 | 1.91 | 23000 | 1925 | 11.94 | 19000 | 2290 | 8.2969 | 10.03 | Split_Wall_Mounted Falcon 1.91TR SEER 10.03 | Split_Wall_Mounted Carrier 1.83TR SEER 10.08
1363 | Split_Wall_Mounted | FISHER | FGSAP-F24C7N | Non-Inverter | 2 | 1.83 | 22000 | [5 empty] | - | Split_Wall_Mounted FISHER 1.83TR SEER - | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
1364 | Split_Wall_Mounted | Frego | S-036H | Non-Inverter | 3 | 3 | 36000 | 3460 | 10.4 |  |  |  | - | Split_Wall_Mounted Frego 3TR SEER - | Split_Wall_Mounted Carrier 2.75TR SEER 8.81
1365 | Split_Wall_Mounted | Frego | FW24X-2A | Non-Inverter | 2 | 1.83 | 22000 | [5 empty] | - | Split_Wall_Mounted Frego 1.83TR SEER - | Split_Wall_Mounted Zamil 2TR SEER 6.69
1366 | Split_Wall_Mounted | Frego | FW24X-2AR | Non-Inverter | 2 | 1.77 | 21300 | [5 empty] | - | Split_Wall_Mounted Frego 1.77TR SEER - | Split_Wall_Mounted LG 1.87TR SEER 7.14
1367 | Split_Wall_Mounted | Frego | FW24X-2N6/FO24X-2N6 | Non-Inverter | 2 | 1.84 | 22178 | 1820 | 12.18 | 19107 | 2200 | 8.685 | 10.34 | Split_Wall_Mounted Frego 1.84TR SEER 10.34 | Split_Wall_Mounted Crown 1.79TR SEER 10.33
1368 | Split_Wall_Mounted | Fuji | RSA24SET | Non-Inverter | 2 | 1.95 | 23500 | 2660 | 8.83 | 20300 | 3150 | 6.4444 | 7.54 | Split_Wall_Mounted Fuji 1.95TR SEER 7.54 | Split_Wall_Mounted LG 1.91TR SEER 7.54
1369 | Split_Wall_Mounted | GIANT | GIANT36CCL | Non-Inverter | 2.5 | 2.45 | 29500 | 2440 | 12.09 | 25500 | 2945 | 8.6587 | 10.27 | Split_Wall_Mounted GIANT 2.45TR SEER 10.27 | Split_Wall_Mounted Carrier 2.25TR SEER 10.20
1370 | Split_Wall_Mounted | General Electric | AS1GC18BD2W | Non-Inverter | 1.5 | 1.58 | 18998.016 | 1610 | 11.8 | 16797.276 | 1910 | 8.7944 | 10.15 | Split_Wall_Mounted General Electric 1.58TR SEER 10.15 | Split_Wall_Mounted LG 1.47TR SEER 10.15
1371 | Split_Wall_Mounted | S.D.General | S.D.G18-B2/EAD | Non-Inverter | 1.5 | 1.5 | 18000 | 1920 | 9.37 | 16600 | 2350 | 7.0638 | 8.12 | Split_Wall_Mounted S.D.General 1.5TR SEER 8.12 | Split_Wall_Mounted LG 1.54TR SEER 8.14
1372 | Split_Wall_Mounted | General Gold | GG18KCN | Non-Inverter | 1.5 | 1.43 | 17180 | 1450 | 11.84 | 15000 | 1750 | 8.5714 | 10.1 | Split_Wall_Mounted General Gold 1.43TR SEER 10.1 | Split_Wall_Mounted LG 1.47TR SEER 10.15
1373 | Split_Wall_Mounted | Gree | GWCN24DCTD1A1A/I | Non-Inverter | 2 | 2.02 | 24300 | [5 empty] | - | Split_Wall_Mounted Gree 2.02TR SEER - | Split_Wall_Mounted Zamil 2TR SEER 6.69
1374 | Split_Wall_Mounted | Gree | GWC36QFXH-D3NTB4B/I | Non-Inverter | 2.5 | 2.68 | 32200 | [5 empty] | - | Split_Wall_Mounted Gree 2.68TR SEER - | Split_Wall_Mounted Royal Temp 2.67TR SEER 7.44
1375 | Split_Wall_Mounted | Gree | GWH36LB-D1NTA8D/I | Non-Inverter | 2.5 | 2.75 | 33000 | [5 empty] | - | Split_Wall_Mounted Gree 2.75TR SEER - | Split_Wall_Mounted Carrier 2.75TR SEER 8.54
1376 | Split_Wall_Mounted | Gree | GWCN24B5TD1LA | Non-Inverter | 2 | 2 | 24000 | 3050 | 7.86 |  |  |  | - | Split_Wall_Mounted Gree 2TR SEER - | Split_Wall_Mounted DAEWOO 2TR SEER 7.86
1377 | Split_Wall_Mounted | Gree | GWC30ACE-D3NTA1D/I | Non-Inverter | 2 | 2.27 | 27300 | [5 empty] | - | Split_Wall_Mounted Gree 2.27TR SEER - | Split_Wall_Mounted Zamil 2.11TR SEER7.24
1378 | Split_Wall_Mounted | YONAN | KT3F-18GWIX | Non-Inverter | 1.5 | 1.53 | 18400 | 1560 | 11.79 | 16600 | 1860 | 8.9247 | 10.21 | Split_Wall_Mounted YONAN 1.53TR SEER 10.21 | Split_Wall_Mounted Ugine 1.48TR SEER 10.23
1379 | Split_Wall_Mounted | Trane | 4MWWCA24T1000AB | Non-Inverter | 2 | 1.75 | 21000 | 1714 | 12.25 | 18000 | 2118 | 8.4986 | 10.31 | Split_Wall_Mounted Trane 1.75TR SEER 10.31 | Split_Wall_Mounted Crown 1.79TR SEER 10.33
1380 | Split_Wall_Mounted | LG | LO242C0 | Inverter | 2 | 1.9 | 22800 | 1839 | 12.39 | 19900 | 2287 | 8.7014 | 10.49 | Split_Wall_Mounted LG 1.9TR SEER 10.49 | Inverter unit "No replacement"
1381 | Split_Wall_Mounted | ugine | UGN24H | Non-Inverter | 2 | 1.79 | 21495.6 | 2528.8941 | 8.5 |  |  |  | - | Split_Wall_Mounted ugine 1.79TR SEER - | Split_Wall_Mounted Carrier 1.79TR SEER 8.31
1382 | Split_Floor_Standing | Gree | GVCN48ADTF1A2A/I | Non-Inverter | 3.5 | 3.5 | 42000 | [5 empty] | - | Split_Floor_Standing Gree 3.5TR SEER - | Split_Floor_Standing Zamil 3.42TR SEER 6.87
1383 | Window | Carrier | 51MSR243M-1S | Non-Inverter | 2 | 1.83 | 22000 | 2530 | 8.69 | 18476 | 2980 | 6.2 | 7.36 | Window Carrier 1.83TR SEER 7.36 | Window Zamil 2TR SEER 7.33
1384 | Window | Carrier | CRVD243M-1B | Non-Inverter | 2 | 2 | 24000 | 2940 | 8.16 |  | 3250 | 0 | - | Window Carrier 2TR SEER - | Window LG 2TR SEER 7.48
1385 | Split_Wall_Mounted | Zamil | MWZ24CCIXFTQ | Non-Inverter | 2 | 1.85 | 22297.42 | 2850 | 7.82 | 19550.76 | 3300 | 5.9245 | 6.76 | Split_Wall_Mounted Zamil 1.85TR SEER 6.76 | Split_Wall_Mounted Zamil 2TR SEER 6.69
1386 | Window | LG | W242SH SN1 | Non-Inverter | 2 | 2 | 24000 | 3000 | 8 | 17401.2 | 3200 | 5.4379 | 6.62 | Window LG 2TR SEER 6.62 | Window Royal Temp 2TR SEER 6.41
1387 | Split_Wall_Mounted | MANDO | MP20T-24C | Non-Inverter | 2 | 1.91 | 23000 | 1917 | 11.99 |  |  |  | - | Split_Wall_Mounted MANDO 1.91TR SEER - | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
1388 | Split_Ceiling_Cassette | Classic | MFX60CSHDAD1 | Non-Inverter | 4.5 | 4.41 | 53000 | 4454 | 11.89 | 46400 | 5524 | 8.3997 | 10.08 | Split_Ceiling_Cassette Classic 4.41TR SEER 10.08 | Split_Ceiling_Cassette LG 4.21TR SEER 7.69
1389 | Split_Ceiling_Cassette | KELON | AS-24CT2FQ | Non-Inverter | 2 |  |  | 2750 | 0 |  |  |  |  | Split_Ceiling_Cassette KELON TR SEER | Split_Ceiling_Cassette Carrier 1.97TR SEER 10.37
1390 | Split_Ceiling_Cassette | ZAMIL | KRZ18CDGC | Non-Inverter | 1.5 | 1.46 | 17599.096 | 1524 | 11.54 | 14398.64 | 1735 | 8.2989 | 9.78 | Split_Ceiling_Cassette ZAMIL 1.46TR SEER 9.78 | Split_Ceiling_Cassette LG 1.5TR SEER 8.05
1391 | Split_Ceiling_Cassette | ZAMIL | KYO24CSRHNAN | Non-Inverter | 2 | [8 empty] | Split_Ceiling_Cassette ZAMIL TR SEER | Split_Ceiling_Cassette Carrier 1.97TR SEER 10.37
1392 | Split_Ceiling_Cassette | LG | LT-C182EL | Non-Inverter | 1.5 | 1.5 | 18000 | 1900 | 9.47 | 15661.08 | 2150 | 7.2842 | 8.21 | Split_Ceiling_Cassette LG 1.5TR SEER 8.21 | Split_Ceiling_Cassette LG 1.5TR SEER 8.05
1393 | Split_Ceiling_Cassette | LG | LT-C242EL | Non-Inverter | 2 | 2 | 24000 | 2500 | 9.6 | 20983.8 | 2830 | 7.4148 | 8.33 | Split_Ceiling_Cassette LG 2TR SEER 8.33 | Split_Ceiling_Cassette LG 2.0TR SEER 8.33
1394 | Split_Ceiling_Cassette | FRIEDRICH | MR24YX6H | Non-Inverter | 2 | [8 empty] | Split_Ceiling_Cassette FRIEDRICH TR SEER | Split_Ceiling_Cassette Carrier 1.97TR SEER 10.37
1395 | Split_Ceiling_Cassette | LG | LT-H182ELEO | Non-Inverter | 1.5 | 1.5 | 18000 | 1900 | 9.47 | 15661.08 | 2150 | 7.2842 | 8.21 | Split_Ceiling_Cassette LG 1.5TR SEER 8.21 | Split_Ceiling_Cassette LG 1.5TR SEER 8.05
1396 | Split_Ceiling_Cassette | Classic | KY030CSRHNANN | Non-Inverter | 2.5 | [8 empty] | Split_Ceiling_Cassette Classic TR SEER | Split_Ceiling_Cassette LG 2.32TR SEER 8.12
1397 | Split_Ceiling_Cassette | LG | LBUH482RSA5 | Non-Inverter | 4 | [8 empty] | Split_Ceiling_Cassette LG TR SEER | Split_Ceiling_Cassette LG 4.21TR SEER 7.69
1398 | Split_Ceiling_Cassette | Classic | KY024CSRHNANN | Non-Inverter | 2 | [8 empty] | Split_Ceiling_Cassette Classic TR SEER | Split_Ceiling_Cassette Carrier 1.97TR SEER 10.37
1399 | Split_Ceiling_Cassette | Classic | KY60MSRHANN | Non-Inverter | 5 | [8 empty] | Split_Ceiling_Cassette Classic TR SEER | No Equivalent Found provide Pic & Datasheets
1400 | Split_Ceiling_Cassette | Zamil | KYA030H | Non-Inverter | 2.5 | 2.25 | 27000 | 2288 | 11.8 | 23000 | 2755 | 8.3485 | 9.98 | Split_Ceiling_Cassette Zamil 2.25TR SEER 9.98 | Split_Ceiling_Cassette LG 2.32TR SEER 8.12
1401 | Split_Ceiling_Cassette | Zamil | KYA048H | Non-Inverter | 4 | [8 empty] | Split_Ceiling_Cassette Zamil TR SEER | Split_Ceiling_Cassette LG 4.21TR SEER 7.69
1402 | Split_Ceiling_Cassette | LG | LS-C382NMM0 | Non-Inverter | 3 | 3.16 | 38000 | 3970 | 9.57 |  |  |  |  | Split_Ceiling_Cassette LG 3.16TR SEER | Split_Ceiling_Cassette Carrier 2.88TR SEER 10.05
1403 | Split_Ceiling_Cassette | Classic | CRC24CDAHIKDA | Non-Inverter | 2 | [8 empty] | Split_Ceiling_Cassette Classic TR SEER | Split_Ceiling_Cassette Carrier 1.97TR SEER 10.37
1404 | Split_Ceiling_Cassette | LG | ATUQ24GNLT0 | Inverter | 2 | 2 | 24000 | 2070 | 11.59 | 19900 | 2070 | 9.6135 | 10.19 | Split_Ceiling_Cassette LG 2TR SEER 10.19 | Inverter unit "No replacement"
1405 | Split_Ceiling_Cassette | GREE | GUTD24W/A-S(S) | Inverter | 2 | [8 empty] | Split_Ceiling_Cassette GREE TR SEER | Inverter unit "No replacement"
1406 | Split_Ceiling_Cassette | GREE | GUTD36W/A-S(S) | Inverter | 3 | [8 empty] | Split_Ceiling_Cassette GREE TR SEER | Inverter unit "No replacement"
1407 | Split_Ceiling_Cassette | LG | ATUW18GPLT2 | Inverter | 1.5 | 1.5 | 18000 | 1450 | 12.41 | 16200 | 1800 | 9 | 10.62 | Split_Ceiling_Cassette LG 1.5TR SEER 10.62 | Inverter unit "No replacement"
1408 | Split_Floor_Standing | Samsung | AP500PF | Non-Inverter | 3.5 | 3.3 | 39683 | 5300 | 7.48 |  |  |  | - | Split_Floor_Standing Samsung 3.3TR SEER - | Split_Floor_Standing LG 3.33TR SEER 8.08
1409 | Split_Floor_Standing | Hisense | AUF60COIN | Inverter | 4.5 | 4.41 | 53000 | 4344 | 12.2 |  |  |  | - | Split_Floor_Standing Hisense 4.41TR SEER - | Inverter unit "No replacement"
1410 | Split_Floor_Standing | Craft | DS60FE7HS7FHM | Non-Inverter | 4.5 | 4.39 | 52746 | 4404 | 11.97 | 45826 | 5454 | 8.4023 | 10.12 | Split_Floor_Standing Craft 4.39TR SEER 10.12 | Split_Floor_Standing Zamil 4.421TR SEER 10.15
1411 | Split_Floor_Standing | Kelvinator | FS-060H | Non-Inverter | 4 | 3.84 | 46089 | 5470 | 8.42 | 42334 | 6380 | 6.6354 | 7.38 | Split_Floor_Standing Kelvinator 3.84TR SEER 7.38 | Split_Floor_Standing LG 3.75TR SEER 7.47
1412 | Split_Floor_Standing | Ugine | KT3F-70L | Non-Inverter | 2 | 1.99 | 23898 | 3200 | 7.46 |  |  |  | - | Split_Floor_Standing Ugine 1.99TR SEER - | No Equivalent Found provide Pic & Datasheets
1413 | Split_Wall_Mounted | Trane | 4MWWCA12T1000AA | Non-Inverter | 1 | 0.99 | 11900 | 1010 | 11.78 | 10100 | 1210 | 8.3471 | 9.97 | Split_Wall_Mounted Trane 0.99TR SEER 9.97 | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
1414 | Split_Wall_Mounted | Trane | 4MWWCA18T1000AA | Non-Inverter | 1.5 | 1.51 | 18200 | 1560 | 11.66 | 16200 | 1850 | 8.7568 | 10.06 | Split_Wall_Mounted Trane 1.51TR SEER 10.06 | Split_Wall_Mounted GREE 1.5TR SEER 9.98
1415 | Split_Wall_Mounted | Trane | 4MWWCA24T1000AA | Non-Inverter | 2 | 1.93 | 23202 | 2000 | 11.6 | 19899 | 2390 | 8.3259 | 9.86 | Split_Wall_Mounted Trane 1.93TR SEER 9.86 | Split_Wall_Mounted LG 1.74TR SEER 9.84
1416 | Split_Wall_Mounted | Trane | 4MWWCA30T1000AA | Non-Inverter | 2.5 | 2.31 | 27800 | 2310 | 12.03 | 24200 | 2740 | 8.8321 | 10.3 | Split_Wall_Mounted Trane 2.31TR SEER 10.3 | Split_Wall_Mounted Zamil 2.24TR SEER 10.35
1417 | Split_Wall_Mounted | Trane | 4MWWCA36T1000AA | Non-Inverter | 2.5 | 2.69 | 32300 | 2710 | 11.91 | 27700 | 3230 | 8.5759 | 10.14 | Split_Wall_Mounted Trane 2.69TR SEER 10.14 | Split_Wall_Mounted Royal Temp 2.67TR SEER 7.44
1418 | Split_Wall_Mounted | Ravo | AC-RAV24CC | Non-Inverter | 2 | 1.79 | 21495 | 1800 | 11.94 | 18425 | 2150 | 8.5698 | 10.15 | Split_Wall_Mounted Ravo 1.79TR SEER 10.15 | Split_Wall_Mounted Carrier 1.84TR SEER 10.16
1419 | Split_Wall_Mounted | Classic | ADO36CCXCD | Non-Inverter | 2.5 | 2.61 | 31400 | 2573 | 12.2 |  |  |  | - | Split_Wall_Mounted Classic 2.61TR SEER - | Split_Wall_Mounted LG 2.5TR SEER 10.43
1420 | Split_Wall_Mounted | Mando | F22M-24CT | Non-Inverter | 2 | 1.87 | 22500 | 1899 | 11.84 | 19300 | 2311 | 8.3514 | 10.02 | Split_Wall_Mounted Mando 1.87TR SEER 10.02 | Split_Wall_Mounted Carrier 1.83TR SEER 10.08
1421 | Split_Wall_Mounted | Gibson | GS24CH | Non-Inverter | 2 | 1.75 | 21040 | 1815 | 11.59 | 17060 | 2055 | 8.3017 | 9.8 | Split_Wall_Mounted Gibson 1.75TR SEER 9.8 | Split_Wall_Mounted LG 1.82TR SEER 9.79
1422 | Split_Wall_Mounted | Zamil | HRZ18CDBCIRDK | Non-Inverter | 1.5 | 1.5 | 18000 | 1481 | 12.15 | 15400 | 1800 | 8.5556 | 10.27 | Split_Wall_Mounted Zamil 1.5TR SEER 10.27 | Split_Wall_Mounted Cooline 1.5TR SEER 10.25
1423 | Split_Wall_Mounted | Mando | MP920-30H | Non-Inverter | 2.5 | 2.25 | 27000 | 2177 | 12.4 |  |  |  | - | Split_Wall_Mounted Mando 2.25TR SEER - | Split_Wall_Mounted Gree 2.25TR SEER 11.11
1424 | Split_Wall_Mounted | Midea | MSTG-24HR-19 | Non-Inverter | 2 | 1.84 | 22191 | 2438 | 9.1 |  |  |  | - | Split_Wall_Mounted Midea 1.84TR SEER - | Split_Wall_Mounted Carrier 2TR SEER 8.60
1425 | Split_Wall_Mounted | Toshiba | RAV-181K2B | Non-Inverter | 1.5 | 1.42 | 17070 | [5 empty] | - | Split_Wall_Mounted Toshiba 1.42TR SEER - | Split_Wall_Mounted LG 1.41TR SEER 6.94
1426 | Split_Wall_Mounted | Toshiba | RAV-241K2B | Non-Inverter | 2 | 1.9 | 22874 | [5 empty] | - | Split_Wall_Mounted Toshiba 1.9TR SEER - | Split_Wall_Mounted Zamil 2TR SEER 6.69
1427 | Split_Wall_Mounted | Toshiba | RAV-457KEE2BD | Non-Inverter | 1.5 | 1.5 | 18000 | [5 empty] | - | Split_Wall_Mounted Toshiba 1.5TR SEER - | Split_Wall_Mounted LG 1.41TR SEER 6.94
1428 | Split_Wall_Mounted | Toshiba | RAV-717KEE2BD | Non-Inverter | 2 | 2 | 24000 | [5 empty] | - | Split_Wall_Mounted Toshiba 2TR SEER - | Split_Wall_Mounted Zamil 2TR SEER 6.69
1429 | Split_Wall_Mounted | Fuji | RSA24FMTA-S | Non-Inverter | 2 | 1.88 | 22600 | 1960 | 11.53 | 19500 | 2350 | 8.2979 | 9.81 | Split_Wall_Mounted Fuji 1.88TR SEER 9.81 | Split_Wall_Mounted LG 1.99TR SEER 9.80
1430 | Split_Wall_Mounted | Speed_Cool | SCIT24H | Non-Inverter | 2 | 1.68 | 20279 | 2628 | 7.71 |  |  |  | - | Split_Wall_Mounted Speed_Cool 1.68TR SEER - | Split_Wall_Mounted Daikin 1.55TR SEER 7.08
1431 | Split_Wall_Mounted | Soft power | SFP-T-24KC19 | Non-Inverter | 2 | 1.75 | 21000 | 1721 | 12.2 |  |  |  | - | Split_Wall_Mounted Soft power 1.75TR SEER - | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
1432 | Split_Wall_Mounted | TCL | TAC-24CS/E7 | Non-Inverter | 2 | 1.75 | 21040 | 1815 | 11.59 |  |  |  | - | Split_Wall_Mounted TCL 1.75TR SEER - | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
1433 | Split_Wall_Mounted | Zamil | TDZ24CCXRD | Non-Inverter | 2 | 1.91 | 23000 | [5 empty] | - | Split_Wall_Mounted Zamil 1.91TR SEER - | Split_Wall_Mounted Zamil 2TR SEER 6.69
1434 | Split_Wall_Mounted | Smart_Electric | WAL30-C-INA1 | Inverter | 2.5 | 2.33 | 28000 | 2231 | 12.55 |  |  |  | - | Split_Wall_Mounted Smart_Electric 2.33TR SEER - | Inverter unit "No replacement"
1435 | Window | Rowa | 024E8Y | Non-Inverter | 2 | 2 | 24000 | 3200 | 7.5 |  |  |  | - | Window Rowa 2TR SEER - | Window LG 2TR SEER 7.48
1436 | Window | Classic | ACB19CTXQIMNW | Non-Inverter | 1.5 | 1.54 | 18500 | 2260 | 8.18 | 14500 | 2630 | 5.5133 | 6.79 | Window Classic 1.54TR SEER 6.79 | Window Zamil 1.5TR SEER 6.80
1437 | Window | Gibson | AO24E8Y | Non-Inverter | 2 | 2 | 24000 | 3200 | 7.5 |  |  |  | - | Window Gibson 2TR SEER - | Window LG 2TR SEER 7.48
1438 | Window | General | AXSA18AATH | Non-Inverter | 1.5 | 1.5 | 18100 | 2200 | 8.22 |  |  |  | - | Window General 1.5TR SEER - | Window Carrier 1.43TR SEER 8.52
1439 | Window | BASIC | BWAC-H18CF | Non-Inverter | 1.5 | 1.5 | 18000 | [5 empty] | 8.65 | Window BASIC 1.5TR SEER 8.65 | Window Carrier 1.5TR SEER 8.62
1440 | Window | Champion | CHVR243M-OS | Non-Inverter | 2 | 1.83 | 22000 | 2600 | 8.46 | 18504 | 3100 | 5.969 | 7.15 | Window Champion 1.83TR SEER 7.15 | Window Zamil 2TR SEER 7.20
1441 | Window | Carrier | CR3M-24H | Non-Inverter | 2 | 2 | 24000 | 2860 | 8.39 |  |  |  | - | Window Carrier 2TR SEER - | Window LG 2TR SEER 7.48
1442 | Window | Carrier | CRVD243M-0B5 | Non-Inverter | 2 | 2 | 24050 | 2813 | 8.54 | 18982 | 3089 | 6.145 | 7.22 | Window Carrier 2TR SEER 7.22 | Window Zamil 2TR SEER 7.22
1443 | Window | Falcon | FQSR183M-OM | Non-Inverter | 1.5 | 1.5 | 18000 | 2200 | 8.18 |  |  |  | - | Window Falcon 1.5TR SEER - | Window Carrier 1.43TR SEER 8.52
1444 | Window | Classic | HHB19CKEFINNW | Non-Inverter | 1.5 | 1.54 | 18500 | 1814 | 10.19 | 14500 | 1986 | 7.3011 | 8.6 | Window Classic 1.54TR SEER 8.6 | Window Carrier 1.5TR SEER 8.62
1445 | Window | York | NYTH19R06 | Non-Inverter | 1.5 | 1.5 | 18000 | 2200 | 8.18 |  |  |  | - | Window York 1.5TR SEER - | Window Carrier 1.5TR SEER 8.62
1446 | Window | York | NYTH24 | Non-Inverter | 2 | 2 | 24000 | [5 empty] | - | Window York 2TR SEER - | Window Zamil 2TR SEER 6.23
1447 | Window | SANIYO | SA185BME6 | Non-Inverter | 1.5 | 1.5 | 18000 | 2620 | 6.87 |  |  |  | - | Window SANIYO 1.5TR SEER - | Window Carrier 1.5TR SEER 8.62
1448 | Window | Zamil | SCB18CRXYIINW | Non-Inverter | 1.5 | 1.5 | 18000 | 2200 | 8.18 | 12500 | 2300 | 5.4348 | 6.71 | Window Zamil 1.5TR SEER 6.71 | Window Zamil 1.5TR SEER 6.80
1449 | Window | Ugine | UAWM18C | Non-Inverter | 1.5 | 1.48 | 17800 | 1745 | 10.2 |  |  |  | - | Window Ugine 1.48TR SEER - | Window Carrier 1.5TR SEER 8.62
1450 | Window | Ugine | UAWMS24C | Non-Inverter | 2 | 1.75 | 21000 | [5 empty] | 8.65 | Window Ugine 1.75TR SEER 8.65 | Window York 1.75TR SEER 8.45
1451 | Window | HEAVY DUTY | WRC 1834K2S | Non-Inverter | 1.5 | 1.5 | 18000 | [5 empty] | - | Window HEAVY DUTY 1.5TR SEER - | Window Carrier 1.5TR SEER 8.62
1452 | Window | White Westinghouse | WWA20G8NR | Non-Inverter | 1.5 | 1.5 | 18000 | 1756 | 10.25 |  |  |  | - | Window White Westinghouse 1.5TR SEER - | Window Carrier 1.5TR SEER 8.62
1453 | Window | Zamil | ZCM24CGXFMNNW1 | Non-Inverter | 2 | 1.75 | 21000 | 2058 | 10.2 | 17800 | 2438 | 7.3011 | 8.66 | Window Zamil 1.75TR SEER 8.66 | Window York 1.75TR SEER 8.45
1454 | Split_Wall_Mounted | Midea | MSTMXV12HRN1AG1 | Inverter | 1 | 1 | 12000 | [6 empty] | Split_Wall_Mounted Midea 1TR SEER | Inverter unit "No replacement"
1455 | Split_Wall_Mounted | Midea | MSTMXV18HRN2AG1 | Inverter | 1.5 | 1.5 | 18000 | [6 empty] | Split_Wall_Mounted Midea 1.5TR SEER | Inverter unit "No replacement"
1456 | Split_Wall_Mounted | Midea | MSTMXV24HRN1AG1 | Inverter | 2 | 2 | 24000 | [6 empty] | Split_Wall_Mounted Midea 2TR SEER | Inverter unit "No replacement"
1457 | Split_Wall_Mounted | Midea | MSTMXV30HRN1AG1 | Inverter | 2.5 | 2.5 | 30000 | [6 empty] | Split_Wall_Mounted Midea 2.5TR SEER | Inverter unit "No replacement"
1458 | Split_Wall_Mounted | Midea | MSTMXV36HRNMB | Inverter | 3 | 3 | 36000 | [6 empty] | Split_Wall_Mounted Midea 3TR SEER | Inverter unit "No replacement"
1459 | Split_Ceiling_Cassette | Midea | MCCTV18HRN2 | Inverter | 1.5 | 1.5 | 18000 | [6 empty] | Split_Ceiling_Cassette Midea 1.5TR SEER | Inverter unit "No replacement"
1460 | Split_Ceiling_Cassette | Midea | MCCTV24HRN3 | Inverter | 2 | 2 | 24000 | [6 empty] | Split_Ceiling_Cassette Midea 2TR SEER | Inverter unit "No replacement"
1461 | Split_Ceiling_Cassette | Midea | MCCTV30HRN1 | Inverter | 2.5 | 2.5 | 30000 | [6 empty] | Split_Ceiling_Cassette Midea 2.5TR SEER | Inverter unit "No replacement"
1462 | Split_Floor_Standing | Midea | MFTGAV50CRN | Inverter | 4 | 4.16 | 50000 | [6 empty] | Split_Floor_Standing Midea 4.16TR SEER | Inverter unit "No replacement"
1463 | Split_Floor_Standing | Midea | MFTGAV50HRN2 | Inverter | 4 | 4.16 | 50000 | [6 empty] | Split_Floor_Standing Midea 4.16TR SEER | Inverter unit "No replacement"
1464 | Window | ALTO | AAN 19CR-5 | Non-Inverter | 1.5 | 1.5 | 18000 | 2200 | 8.18 |  |  |  |  | Window ALTO 1.5TR SEER | Window Carrier 1.43TR SEER 8.52
1465 | Window | Zamil | ACB19CAXQIMNW | Non-Inverter | 1.5 | 1.5 | 18000 | 2370 | 7.59 | 15000 | 2770 | 5.4152 | 6.43 | Window Zamil 1.5TR SEER 6.43 | Window Zamil 1.5TR SEER 6.51
1466 | Window | Zamil | AHB19CEDW | Non-Inverter | 1.5 | 1.5 | 18000 | 2100 | 8.57 | 15000 | 2370 | 6.3291 | 7.32 | Window Zamil 1.5TR SEER 7.32 | Window LG 1.49TR SEER 7.24
1467 | Window | Zamil | AHB19CREPIINW | Non-Inverter | 1.5 | 1.54 | 18500 | 2200 | 8.4 | 13500 | 2250 | 6 | 7.05 | Window Zamil 1.54TR SEER 7.05 | Window LG 1.39TR SEER 7.03
1468 | Window | Zamil | AHB24CREPIINW | Non-Inverter | 2 | 2 | 24000 | 2800 | 8.57 | 18000 | 3100 | 5.8065 | 7.1 | Window Zamil 2TR SEER 7.1 | Window Zamil 2TR SEER 7.10
1469 | Window | SAMSUNG | AHT18F1HBB | Non-Inverter | 1.5 | 1.5 | 18000 | 2050 | 8.78 | 14484 | 2200 | 6.5836 | 7.51 | Window SAMSUNG 1.5TR SEER 7.51 | Window LG 1.5TR SEER 7.70
1470 | Window | SAMSUNG | AHT18WIE | Non-Inverter | 1.5 | 1.5 | 18000 | 2200 | 8.18 | 14490 | 2550 | 5.6824 | 6.86 | Window SAMSUNG 1.5TR SEER 6.86 | Window Samsung 1.5TR SEER 6.82
1471 | Window | HISENSE | AW17HT | Non-Inverter | 1.5 | 1.41 | 17000 | 1626 | 10.45 |  |  |  |  | Window HISENSE 1.41TR SEER | Window Carrier 1.5TR SEER 8.62
1472 | Window | FUJITSU | AXS18RANHW | Non-Inverter | 1.5 | 1.5 | 18000 | 2180 | 8.25 | 13648 | 2570 | 5.3105 | 6.75 | Window FUJITSU 1.5TR SEER 6.75 | Window Zamil 1.5TR SEER 6.80
1474 | Window | Carrier | C2K24HMB | Non-Inverter | 2 | 2 | 24000 | 2800 | 8.57 | 18698 | 3000 | 6.2327 | 7.26 | Window Carrier 2TR SEER 7.26 | Window Zamil 2TR SEER 7.24
1475 | Window | Carrier | CR18HK5 | Non-Inverter | 1.5 | 1.33 | 16000 | 2200 | 7.27 |  |  |  |  | Window Carrier 1.33TR SEER | Window LG 1.39TR SEER 7.03
1476 | Window | Carrier | CR3M-18HK5 | Non-Inverter | 1.5 | 1.5 | 18000 | 2200 | 8.18 |  |  |  |  | Window Carrier 1.5TR SEER | Window Carrier 1.43TR SEER 8.52
1477 | Window | CARRIER | CRSD243M-0B5 | Non-Inverter | 2 | 2 | 24050 | 2813 | 8.54 | 19000 | 3089 | 6.1509 | 7.23 | Window CARRIER 2TR SEER 7.23 | Window Zamil 2TR SEER 7.24
1478 | Window | LG | D182EH SN2 | Non-Inverter | 1.5 | 1.51 | 18200 | 1785 | 10.19 | 15200 | 2117 | 7.18 | 8.6 | Window LG 1.51TR SEER 8.6 | Window Carrier 1.5TR SEER 8.62
1479 | Window | DAEWOO | DWA-181C | Non-Inverter | 1.5 | 1.5 | 18000 | 2150 | 8.37 | 14330 | 2600 | 5.5115 | 6.91 | Window DAEWOO 1.5TR SEER 6.91 | Window Zamil 1.5TR SEER 6.92
1480 | Window | Falcon | FCRL3-18HK5 | Non-Inverter | 1.5 | 1.5 | 18000 | 2200 | 8.18 |  |  |  |  | Window Falcon 1.5TR SEER | Window Carrier 1.43TR SEER 8.52
1481 | Window | GENERAL | GS 1819C | Non-Inverter | 1.5 | 1.41 | 17000 | 1650 | 10.3 |  |  |  |  | Window GENERAL 1.41TR SEER | Window Carrier 1.5TR SEER 8.62
1482 | Window | GENERAL | GS 2430C | Non-Inverter | 2 | 1.83 | 22000 | 2156 | 10.2 |  |  |  |  | Window GENERAL 1.83TR SEER | Window York 1.75TR SEER 8.45
1483 | Window | HISENSE | HW18CA23 | Non-Inverter | 1.5 | 1.5 | 18000 | [5 empty] | 8.65 | Window HISENSE 1.5TR SEER 8.65 | Window Zamil 1.5TR SEER 6.51
1484 | Window | Zamil | LHB19CTECIING | Non-Inverter | 1.5 | 1.5 | 18000 | 2150 | 8.37 | 13750 | 2350 | 5.8511 | 7 | Window Zamil 1.5TR SEER 7 | Window LG 1.39TR SEER 7.03
1485 | Window | YORK | LRC 24H06 | Non-Inverter | 2 | 2 | 24000 | 3200 | 7.5 |  |  |  |  | Window YORK 2TR SEER | Window LG 2TR SEER 7.48
1486 | Window | LG | LWH182MGABO | Non-Inverter | 1.5 | 1.5 | 18000 | 2020 | 8.91 |  |  |  |  | Window LG 1.5TR SEER | Window Carrier 1.5TR SEER 8.62
1487 | Window | LG | LWM1820BHP | Non-Inverter | 1.5 | 1.5 | 18000 | 2020 | 8.91 |  |  |  |  | Window LG 1.5TR SEER | Window Carrier 1.5TR SEER 8.62
1488 | Window | Zamil | MH1950FA | Non-Inverter | 1.5 | 1.62 | 19500 |  |  | 15100 |  |  |  | Window Zamil 1.62TR SEER | Window Zamil 1.5TR SEER 6.51
1489 | Window | LG | W182EH SA0 | Non-Inverter | 1.5 | 1.5 | 18000 | 2120 | 8.49 | 13307 | 2390 | 5.5678 | 6.97 | Window LG 1.5TR SEER 6.97 | Window Zamil 1.5TR SEER 6.92
1490 | Window | LG | W182EH SN0 | Non-Inverter | 1.5 | 1.39 | 16719 | 2000 | 8.35 | 13478 | 2290 | 5.8856 | 7.03 | Window LG 1.39TR SEER 7.03 | Window LG 1.39TR SEER 7.03
1491 | Window | LG | W182EH SN2 | Non-Inverter | 1.5 | 1.39 | 16719 | 2050 | 8.15 | 13990 | 2350 | 5.9532 | 6.95 | Window LG 1.39TR SEER 6.95 | Window LG 1.39TR SEER 7.03
1492 | Window | WHITE | WWA25G6HR | Non-Inverter | 2 | 1.79 | 21500 | 2130 | 10.09 | 17900 | 2510 | 7.1315 | 8.52 | Window WHITE 1.79TR SEER 8.52 | Window York 1.75TR SEER 8.45
1493 | Window | LG | Z182EH SN4 | Non-Inverter | 1.5 | 1.49 | 17948 | 2110 | 8.5 | 15116 | 2460 | 6.1447 | 7.23 | Window LG 1.49TR SEER 7.23 | Window LG 1.49TR SEER 7.24
1494 | Window | Zamil | ZHB18CAEQMNW | Non-Inverter | 1.5 | 1.45 | 17500 | 2330 | 7.51 | 14500 | 2630 | 5.5133 | 6.4 | Window Zamil 1.45TR SEER 6.4 | Window Zamil 1.5TR SEER 6.51
1495 | Window | Zamil | ZHB18CAETIMNW | Non-Inverter | 1.5 | 1.5 | 18000 | 1857 | 9.69 | 15000 | 2149 | 6.98 | 8.23 | Window Zamil 1.5TR SEER 8.23 | Window Carrier 1.43TR SEER 8.52
1496 | Window | Zamil | ZHB18CTEYIMNW | Non-Inverter | 1.5 | 1.5 | 18000 | 2250 | 8 | 13500 | 2650 | 5.0943 | 6.52 | Window Zamil 1.5TR SEER 6.52 | Window Zamil 1.5TR SEER 6.51
1497 | Window | Zamil | ZHB24CTEYIMNW | Non-Inverter | 2 | 2 | 24000 | 2740 | 8.75 | 18000 | 3200 | 5.625 | 7.16 | Window Zamil 2TR SEER 7.16 | Window Zamil 2TR SEER 7.20
1498 | Split_Wall_Mounted | LG | LO242H0 | Non-Inverter | 2 | 1.87 | 22500 | 1815 | 12.39 | 19300 | 2218 | 8.7015 | 10.47 | Split_Wall_Mounted LG 1.87TR SEER 10.47 | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
1500 | Split_Wall_Mounted | LG | S242 NH STG | Non-Inverter | 2 | 1.91 | 22997 | 2630 | 8.74 | 20063 | 3035 | 6.6105 | 7.54 | Split_Wall_Mounted LG 1.91TR SEER 7.54 | Split_Wall_Mounted LG 1.91TR SEER 7.54
1501 | Split_Wall_Mounted | Coolsense | AAMJCSP18SAH | Non-Inverter | 1.5 | 1.5 | 18000 | 1450 | 12.41 | 15900 | 1740 | 9.1379 | 10.65 | Split_Wall_Mounted Coolsense 1.5TR SEER 10.65 | Split_Wall_Mounted Zamil 1.49TR SEER 10.52
1502 | Split_Wall_Mounted | SAMSUNG | A18TUNN | Non-Inverter | 1.5 | 1.5 | 18000 | 1900 | 9.47 |  |  |  |  | Split_Wall_Mounted SAMSUNG 1.5TR SEER | Split_Wall_Mounted LG 1.46TR SEER 9.8
1503 | Split_Wall_Mounted | SAMSUNG | AS36UGBN | Non-Inverter | 2.5 | 2.75 | 33000 | 3800 | 8.68 | 28175 | 3950 | 7.1329 | 7.64 | Split_Wall_Mounted SAMSUNG 2.75TR SEER 7.64 | Split_Wall_Mounted Royal Temp 2.5TR SEER 7.53
1504 | Split_Wall_Mounted | LG | B1824H N50 | Non-Inverter | 2 | 1.45 | 17503 | 1520 | 11.51 | 15184 | 1830 | 8.2973 | 9.8 | Split_Wall_Mounted LG 1.45TR SEER 9.8 | Split_Wall_Mounted LG 1.46TR SEER 9.8
1505 | Split_Wall_Mounted | LG | B1824H N51 | Non-Inverter | 2 | 1.45 | 17469 | 1510 | 11.56 | 14978 | 1800 | 8.3211 | 9.84 | Split_Wall_Mounted LG 1.45TR SEER 9.84 | Split_Wall_Mounted LG 1.45TR SEER 9.84
1506 | Split_Wall_Mounted | MANDO | F22M-18HT | Non-Inverter | 1.5 | 1.51 | 18200 | 1517 | 11.99 |  |  |  |  | Split_Wall_Mounted MANDO 1.51TR SEER | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
1507 | Split_Wall_Mounted | MANDO | F22M-24HT | Non-Inverter | 2 | 1.87 | 22500 | 1899 | 11.84 |  |  |  |  | Split_Wall_Mounted MANDO 1.87TR SEER | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
1508 | Split_Wall_Mounted | MANDO | F23TP-18HT | Non-Inverter | 1.5 | 1.51 | 18200 | 1517 | 11.99 |  |  |  | 10.2 | Split_Wall_Mounted MANDO 1.51TR SEER 10.2 | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
1509 | Split_Wall_Mounted | Mando | F23TP-24HT | Non-Inverter | 2 | 1.87 | 22500 | 1899 | 11.84 |  |  |  |  | Split_Wall_Mounted Mando 1.87TR SEER | Split_Wall_Mounted Supergeneral 1.83TR SEER 10.43
1510 | Split_Wall_Mounted | Falcon | FQS18C6 | Non-Inverter | 1.5 | 1.42 | 17100 | 1380 | 12.39 | 14500 | 1665 | 8.7087 | 10.46 | Split_Wall_Mounted Falcon 1.42TR SEER 10.46 | Split_Wall_Mounted LG 1.5TR SEER 10.46
1511 | Split_Wall_Mounted | Falcon | FTS18C4 | Non-Inverter | 1.5 | 1.5 | 18000 | [5 empty] | 10.2 | Split_Wall_Mounted Falcon 1.5TR SEER 10.2 | Split_Wall_Mounted LG 1.41TR SEER 6.94
1512 | Split_Wall_Mounted | Falcon | HBPUC 24 | Non-Inverter | 2 | 2 | 24000 | 3000 | 8 |  |  |  |  | Split_Wall_Mounted Falcon 2TR SEER | Split_Wall_Mounted Carrier 1.81TR SEER 7.91
1513 | Split_Wall_Mounted | YORK | HTKA24OS-ADR | Non-Inverter | 2 | 2 | 24000 | [6 empty] | Split_Wall_Mounted YORK 2TR SEER | Split_Wall_Mounted Zamil 2TR SEER 6.69
1514 | Split_Wall_Mounted | Kelvinator | HBPUDC24 | Non-Inverter | 2 | 2 | 24000 | [6 empty] | Split_Wall_Mounted Kelvinator 2TR SEER | Split_Wall_Mounted Zamil 2TR SEER 6.69
1515 | Split_Wall_Mounted | AKAI | AS13UXIH | Non-Inverter | 1 | 1 | 12000 | 1020 | 11.76 | 10600 | 1260 | 8.4127 | 10.1 | Split_Wall_Mounted AKAI 1TR SEER 10.1 | Split_Wall_Mounted Carrier 0.96TR SEER 10.37
1516 | Split_Wall_Mounted | Zamil | HWX30EHAYFR | Non-Inverter | 2.5 | 2.21 | 26594 | 3020 | 8.8 | 21994 | 3500 | 6.284 | 7.45 | Split_Wall_Mounted Zamil 2.21TR SEER 7.45 | Split_Wall_Mounted LG 2.21TR SEER 7.49
1517 | Split_Wall_Mounted | Comfort Line | MSAC-18CS/XT7 | Non-Inverter | 1.5 | 1.5 | 18000 | 1524 | 11.81 |  |  |  |  | Split_Wall_Mounted Comfort Line 1.5TR SEER | Split_Wall_Mounted Zamil 1.49TR SEER 10.96
1520 | Split_Wall_Mounted | LG | S182SH N52 | Non-Inverter | 1.5 | 1.41 | 17026 | 2100 | 8.1 | 14672 | 2450 | 5.9886 | 6.95 | Split_Wall_Mounted LG 1.41TR SEER 6.95 | Split_Wall_Mounted LG 1.41TR SEER 6.94
1521
1522
1523
1524
1525
1526
1527
1528
1529
1530
1531
1532
1533
1534
1535
1536
1537
1538
1539
1540
1541
1542
1543
1544
1545
1546
1547
1548
1549
1550
1551
1552
1553
1554
1555
1556
1557
1558
1559
1560
1561
1562
1563
1564
1565
1566
1567
1568
1569
1570
1571
1572
1573
1574
1575
1576
1577
1578
1579
1580
1581
1582
1583
1584
1585
1586
1587
1588
1589
1590
1591
1592
1593
1594
1595
1596
1597
1598
1599
1600
1601
1602
1603
1604
1605
1606
1607
1608
1609
1610
1611
1612
1613
1614
1615
1616
1617
1618
1619
1620
1621
1622
1623
1624
1625
1626
1627
1628
1629
1630
1631
1632
1633
1634
1635
1636
1637
1638
1639
1640
1641
1642
1643
1644
1645
1646
1647
1648
1649
1650
1651
1652
1653
1654
1655
1656
1657
1658
1659
1660
1661
1662
1663
1664
1665
1666
1667
1668
1669
1670
1671
1672
1673
1674
1675
1676
1677
1678
1679
1680
1681
1682
1683
1684
1685
1686
1687
1688
1689
1690
1691
1692
1693
1694
1695
1696
1697
1698
1699
1700
1701
1702
1703
1704
1705
1706
1707
1708
1709
1710
1711
1712
1713
1714
1715
1716
1717
1718
1719
1720
1721
1722
1723
1724
1725
1726
1727
1728
1729
1730
1731
1732
1733
1734
1735
1736
1737
1738
1739
1740
1741
1742
1743
1744
1745
1746
1747
1748
1749
1750
1751
1752
1753
1754
1755
1756
1757
1758
1759
1760
1761
1762
1763
1764
1765
1766
1767
1768
1769
1770
1771
1772
1773
1774
1775
1776
1777
1778
1779
1780
1781
1782
1783
1784
1785
1786
1787
1788
1789
1790
1791
1792
1793
1794
1795
1796
1797
1798
1799
1800
1801
1802
1803
1804
1805
1806
1807
1808
1809
1810
1811
1812
1813
1814
1815
1816
1817
1818
1819
1820
1821
1822
1823
1824
1825
1826
1827
1828
1829
1830
1831
1832
1833
1834
1835
1836
1837
1838
1839
1840
1841
1842
1843
1844
1845
1846
1847
1848
1849
1850
1851
1852
1853
1854
1855
1856
1857
1858
1859
1860
1861
1862
1863
1864
1865
1866
1867
1868
1869
1870
1871
1872
1873
1874
1875
1876
1877
1878
1879
1880
1881
1882
1883
1884
1885
1886
1887
1888
1889
1890
1891
1892
1893
1894
1895
1896
1897
1898
1899
1900
1901
1902
1903
1904
1905
1906
1907
1908
1909
1910
1911
1912
1913
1914
1915
1916
1917
1918
1919
1920
1921
1922
1923
1924
1925
1926
1927
1928
1929
1930
1931
1932
1933
1934
1935
1936
1937
1938
1939
1940
1941
1942
1943
1944
1945
1946
1947
1948
1949
1950
1951
1952
1953
1954
1955
1956
1957
1958
1959
1960
1961
1962
1963
1964
1965
1966
1967
1968
1969
1970
1971
1972
1973
1974
1975
1976
1977
1978
1979
1980
1981
1982
1983
1984
1985
1986
1987
1988
1989
1990
1991
1992
1993
1994
1995
1996
1997
1998
1999
2000
2001
2002
2003
2004
2005
2006
2007
2008
2009
2010
2011
2012
2013
2014
2015
2016
2017
2018
2019
2020
2021
2022
2023
2024
2025
2026
2027
2028
2029
2030
2031
2032
2033
2034
2035
2036
2037
2038
2039
2040
2041
2042
2043
2044
2045
2046
2047
2048
2049
2050
2051
2052
2053
2054
2055
2056
2057
2058
2059
2060
2061
2062
2063
2064
2065
2066
2067
2068
2069
2070
2071
2072
2073
2074
2075
2076
2077
2078
2079
2080
2081
2082
2083
2084
2085
2086
2087
2088
2089
2090
2091
2092
2093
2094
2095
2096
2097
2098
2099
2100
2101
2102
2103
2104
2105
2106
2107
2108
2109
2110
2111
2112
2113
2114
2115
2116
2117
2118
2119
2120
2121
2122
2123
2124
2125
2126
2127
2128
2129
2130
2131
2132
2133
2134
2135
2136
2137
2138
2139
2140
2141
2142
2143
2144
2145
2146
2147
2148
2149
2150
2151
2152
2153
2154
2155
2156
2157
2158
2159
2160
2161
2162
2163
2164
2165
2166
2167
2168
2169
2170
2171
2172
2173
2174
2175
2176
2177
2178
2179
2180
2181
2182
2183
2184
2185
2186
2187
2188
2189
2190
2191
2192
2193
2194
2195
2196
2197
2198
2199
2200
2201
2202
2203
2204
2205
2206
2207
2208
2209
2210
2211
2212
2213
2214
2215
2216
2217
2218
2219
2220
2221
2222
2223
2224
2225
2226
2227
2228
2229
2230
2231
2232
2233
2234
2235
2236
2237
2238
2239
2240
2241
2242
2243
2244
2245
2246
2247
2248
2249
2250
2251
2252
2253
2254
2255
2256
2257
2258
2259
2260
2261
2262
2263
2264
2265
2266
2267
2268
2269
2270
2271
2272
2273
2274
2275
2276
2277
2278
2279
2280
2281
2282
2283
2284
2285
2286
2287
2288
2289
2290
2291
2292
2293
2294
2295
2296
2297
2298
2299
2300
2301
2302
2303
2304
2305
2306
2307
2308
2309
2310
2311
2312
2313
2314
2315
2316
2317
2318
2319
2320
2321
2322
2323
2324
2325
2326
2327
2328
2329
2330
2331
2332
2333
2334
2335
2336
2337
2338
2339
2340
2341
2342
2343
2344
2345
2346
2347
2348
2349
2350
2351
2352
2353
2354
2355
2356
2357
2358
2359
2360
2361
2362
2363
2364
2365
2366
2367
2368
2369
2370
2371
2372
2373
2374
2375
2376
2377
2378
2379
2380
2381
2382
2383
2384
2385
2386
2387
2388
2389
2390
2391
2392
2393
2394
2395
2396
2397
2398
2399
2400
2401
2402
2403
2404
2405
2406
2407
2408
2409
2410
2411
2412
2413
2414
2415
2416
2417
2418
2419
2420
2421
2422
2423
2424
2425
2426
2427
2428
2429
2430
2431
2432
2433
2434
2435
2436
2437
2438
2439
2440
2441
2442
2443
2444
2445
2446
2447
2448
2449
2450
2451
2452
2453
2454
2455
2456
2457
2458
2459
2460
2461
2462
2463
2464
2465
2466
2467
2468
2469
2470
2471
2472
2473
2474
2475
2476
2477
2478
2479
2480
2481
2482
2483
2484
2485
2486
2487
2488
2489
2490
2491
2492
2493
2494
2495
2496
2497
2498
2499
2500
2501
2502
2503

## Mnu
|  | Window | Split_Wall_Mounted | Split_Floor_Standing | Split_Ceiling_Cassette | Split_Ceiling_Ducted | Package_Unit
A/C Unit Type |  | York | Zamil | Alessa | Carrier | Carrier | #VALUE!
Window | Non-Inverter | Zamil | ACB | Arrow | Classic | LG
Split_Wall_Mounted | Inverter | AlESSA | Akai | Awalgulf | Classic | York
Split_Floor_Standing |  | ALTO | Alessa | Basic | Craft | Zamil
Split_Ceiling_Cassette | Yes | Amana | AMAX | Carrier | FRIEDRICH
Split_Ceiling_Ducted | No | ARROW | ARROW | Century | General
Package_Unit |  | BASIC | Arven | Classic | Goodman
|  | Carrier | Aukia | Comfort line | Gree
|  | Champion | AUX | Craft | KELON
Size Category | Time | Classic | Awalgulf | Daewoo | LG
1 | 0:00 | Coolsense | Bancool | Falcon | Mando
1.5 | 0:30 | Craft | BASIC | Frego | Midea
2 | 1:00 | DAEWOO | Beko | General | Mitsubishi
2.5 | 1:30 | Falcon | BeSat | GoldStar | Royal_Temp
3 | 2:00 | Fisher | Blue power | Gree | Samsung
3.5 | 2:30 | Frego | BOSCH | Haam | Sky star
4 | 3:00 | Friedrich | Carrier | Haas | Ugine
4.5 | 3:30 | FUJITSU | Caus | Hisense | York
5 | 4:00 | General | Champion | Kelvinator | Zamil
5.5 | 4:30 | General | Champion | LAKES
| 5:00 | General Electric | Chigo | LG
| 5:30 | General_Supreme | Class | Mando
| 6:00 | GIBSON | Class pro | Midea
| 6:30 | Gree | Classic | Mitsubishi
| 7:00 | Haam | Comfort | Rheem
| 7:30 | Haas | Comfort line | Samsung
| 8:00 | HEAVY DUTY | Coolex | SkyStar
| 8:30 | HISENSE | Cooline | Ugine
| 9:00 | Horizon | Coolsense | Winner
| 9:30 | Hotpoint | Craft | York
| 10:00 | Hyundai | CRONY | Zamil
| 10:30 | Kelvinator | Crown
| 11:00 | LG | Daewoo
| 11:30 | Mando | Daikin
| 12:00 | MESTCOOL | DAIYA
| 12:30 | Midea | Dansat
| 13:00 | National | EMJOI
| 13:30 | Other | Eurostar
| 14:00 | QUEEN | Falcon
| 14:30 | QUEEN | Fisher
| 15:00 | Rowa | flix
| 15:30 | Royal_Temp | Frego
| 16:00 | Samsung | Fuji
| 16:30 | SANIYO | Gaint
| 17:00 | Sharp | Galanz
| 17:30 | Shogun | General
| 18:00 | Starway | General Electric
| 18:30 | Super_General | General Electric
| 19:00 | TCL | General Gold
| 19:30 | TIT | GENERAL GOLDIN
| 20:00 | Toshiba | GENERAL PLUS
| 20:30 | Toshiba | General_Supreme
| 21:00 | Ugine | Giant
| 21:30 | WHITE | Gibson
| 22:00 | White Westinghouse | Gold_Eleteca
| 22:30 | York | GoldStar
| 23:00 | Zamil | Gree
| 23:30 |  | Haam
| 24:00 |  | Haas
Haier
HI Home
Hisense
Hitachi
HomeQueen
Icone
IPX4
KAYAN
Kayannenergy
KELON
Kelvinator
Kimatsu
Kleenair
KOOLEN
Lakes
LG
LUNA
Mando
Master_Cool
Matco
MAU
Max plus
Midea
Mitsubishi
MTC
NA
New_house
NIKAI
Noon
O2
Okia
omnia
Panasonic
Panorama
Pearl
Petra
PlasmaGold
Platinum
QUEEN
Queen
RANTIC
RAVO
ROLLC
Rowa
Royal_Temp
S.D.General
SAC
Samsung
sharp
SKM
Sky star
SkyStar
Smart_Electric
Soft power
Speed_Cool
SPEEDCOOL
SREEN
Starway
Super_General
TACHIAIR
TCL
Telezone
TERIM
TIT
TOPTEC
Toshiba
Trane
TRIM
Ugine
Ugne
ultra Plus
Union
Unionaire
Unistar
Unix
WBOX
White Westinghouse
YOKO
YONAN
York
Zamil
ZTRUST

## Vstack
Description | Equipment Type | ID/OD | Make | T1 BTU | in TR | SEER | C&H

## Project_AC List
1.5 TR Window AC Models List (Inverter Units only) | [8 empty] | 2.0 TR Window AC Models List | [8 empty] | 1.0 TR Split_Wall_Mounted AC Models List | [8 empty] | 1.5 TR Split- Wall mounted AC Models List | [8 empty] | 2.0 TR Split- Wall mounted AC Models List | [8 empty] | 2.5 - 3.0 TR Split- Wall mounted AC Models List | [8 empty] | 4.0-5.0 TR Split_Floor_Standing AC Models List
Sl.No | Description / File Name | Equipment Type | ID/OD | Make | T1 BTU | in TR | SEER | C&H | Sl.No | Description / File Name | Equipment Type | ID/OD | Make | T1 BTU | in TR | SEER | C&H | Sl.No | Description / File Name | Equipment Type | ID/OD | Make | T1 BTU | in TR | SEER | C&H | Sl.No | Description / File Name | Equipment Type | ID/OD | Make | T1 BTU | in TR | SEER | C&H | Sl.No | Description / File Name | Equipment Type | ID/OD | Make | T1 BTU | in TR | SEER | C&H | Sl.No | Description / File Name | Equipment Type | ID/OD | Make | T1 BTU | in TR | SEER | C&H | Sl.No | Description / File Name | Equipment Type | ID/OD | Make | T1 BTU | in TR | SEER | C&H
1 | Window Midea 1.47TR SEER 11.05 C&H | Window | WDV18HWG | Midea | 17600 | 1.47 | 11.05 | C&H | 1 | Window Midea 1.71TR SEER 11.1 C | Window | WDV24CWG | Midea | 20500 | 1.71 | 11.1 | C | 1 | Split_Wall_Mounted Midea 0.97TR SEER 15.65 C&H | Split_Wall_Mounted | MSTMXV12HRN1AG1 | Midea | 11600 | 0.97 | 15.65 | C&H | 1 | Split_Wall_Mounted Midea 1.45TR SEER 15 C&H | Split_Wall_Mounted | MSTMXV18HRN2AG1 | Midea | 17400 | 1.45 | 15 | C&H | 1 | Split_Wall_Mounted Basic 1.77TR SEER 15.05 C&H | Split_Wall_Mounted | BSACMA-FI24HB - BSACMA-CI24HB | Basic | 21200 | 1.77 | 15.05 | C&H | 1 | Split_Wall_Mounted Zamil 2.25TR SEER 15.05 C&H | Split_Wall_Mounted | MEZ30CHIVBK | Zamil | 27000 | 2.25 | 15.05 | C&H | 1 | Split_Floor_Standing LG 3.83TR SEER 15.05 C&H V.1 | Split_Floor_Standing | APNW55GT3M6 / AUUW55GT6 | LG | 46000 | 3.83 | 15.05 | C&H
2 | Window Zamil 1.5TR SEER 11.15 C&H V.1 | Window | ZHT18CSEDMNW | Zamil | 18000 | 1.5 | 11.15 | C&H | 2 | Window Zamil 1.8TR SEER 8.6 C&H V.1 | Window | LHH24CGEFMNNW | Zamil | 21600 | 1.8 | 8.6 | C&H | 2 | Split_Wall_Mounted Basic 1TR SEER 15.85 C V.1 | Split_Wall_Mounted | BSACQ-FI12CB | Basic | 12000 | 1 | 15.85 | C | 2 | Split_Wall_Mounted LG 1.5TR SEER 15.2 C V.1 | Split_Wall_Mounted | NS182C2SK1 | LG | 18000 | 1.5 | 15.2 | C | 2 | Split_Wall_Mounted Gree 1.83TR SEER 15 C&H | Split_Wall_Mounted | GWH24AGE-S3DTA1F | Gree | 22000 | 1.83 | 15 | C&H | 2 | Split_Wall_Mounted Midea 2.25TR SEER 15.05 C&H | Split_Wall_Mounted | MSTMXV30HRN2AG1 | Midea | 27000 | 2.25 | 15.05 | C&H | 2 | Split_Floor_Standing Basic 4TR SEER 15.05 C&H V.1 | Split_Floor_Standing | BVAC-FH48HPIB | Basic | 48000 | 4 | 15.05 | C&H
3 | Window Midea 1.5TR SEER 11.4 C | Window | WDV18CWG | Midea | 18000 | 1.5 | 11.4 | C | 3 | Window Basic 1.8TR SEER 8.65 C&H | Window | BWAC-H24HF | Basic | 21600 | 1.8 | 8.65 | C&H | 3 | Split_Wall_Mounted Basic 1TR SEER 15.75 C&H V.1 | Split_Wall_Mounted | BSACQ-FI12HB | Basic | 12000 | 1 | 15.75 | C&H | 3 | Split_Wall_Mounted Basic 1.5TR SEER 15 C&H | Split_Wall_Mounted | BSACQ-FI18HC | Basic | 18000 | 1.5 | 15 | C&H | 3 | Split_Wall_Mounted Zamil 1.83TR SEER 15.05 C V.1 | Split_Wall_Mounted | HIZ24 | Zamil | 22000 | 1.83 | 15.05 | C | 3 | Split_Wall_Mounted Gree 2.28TR SEER 15 C&H | Split_Wall_Mounted | GWH30AGEXH-S3DTA1A | Gree | 27400 | 2.28 | 15 | C&H | 3 | Split_Floor_Standing Basic 4TR SEER 15 C&H | Split_Floor_Standing | BVAC-FH48HPIC | Basic | 48000 | 4 | 15 | C&H
4 | Window Zamil 1.5TR SEER 11.2 C V.2 | Window | RCT18CSXDMNNW | Zamil | 18000 | 1.5 | 11.2 | C | 4 | Window Basic 1.82TR SEER 8.65 C | Window | BWAC-H24CF | Basic | 21800 | 1.82 | 8.65 | C | 4 | Split_Wall_Mounted LG 1TR SEER 15.1 C V.1 | Split_Wall_Mounted | NF122C0.NJ0 | LG | 12000 | 1 | 15.1 | C | 4 | Split_Wall_Mounted Basic 1.5TR SEER 15.3 C | Split_Wall_Mounted | BSACMA-FI18CB | Basic | 18000 | 1.5 | 15.3 | C | 4 | Split_Wall_Mounted Gree 1.83TR SEER 15 C | Split_Wall_Mounted | GWH24AGE-S3DTA1F/I | Gree | 22000 | 1.83 | 15 | C | 4 | Split_Wall_Mounted Zamil 2.28TR SEER 15 C V.1 | Split_Wall_Mounted | HIZ30 | Zamil | 27400 | 2.28 | 15 | C | 4 | Split_Floor_Standing Hisense 4TR SEER 15.05 C&H | Split_Floor_Standing | HUF48HAI/O23 | Hisense | 48000 | 4 | 15.05 | C&H
5 | Window Zamil 1.5TR SEER 11.2 C V.1 | Window | ZCT18CSXDMNNW | Zamil | 18000 | 1.5 | 11.2 | C | 5 | Window Hisense 1.82TR SEER 8.65 C | Window | HW24CA23 | Hisense | 21800 | 1.82 | 8.65 | C | 5 | Split_Wall_Mounted Basic 1TR SEER 15 C | Split_Wall_Mounted | BSACMA-FI12CB | Basic | 12000 | 1 | 15 | C | 5 | Split_Wall_Mounted Zamil 1.5TR SEER 15.05 C V.1 | Split_Wall_Mounted | HIZ18 | Zamil | 18000 | 1.5 | 15.05 | C | 5 | Split_Wall_Mounted Haier 1.83TR SEER 15.05 C&H | Split_Wall_Mounted | HSU-24HPA13/R2 (T3DBN-B) | Haier | 22000 | 1.83 | 15.05 | C&H | 5 | Split_Wall_Mounted Gree 2.28TR SEER 15 C | Split_Wall_Mounted | GWC30AGEXH‐S3DTA1A/I | Gree | 27400 | 2.28 | 15 | C | 5 | Split_Floor_Standing Basic 4.58TR SEER 13.9 C&H V.1 | Split_Floor_Standing | BVAC-FH60HPIC | Basic | 55000 | 4.58 | 13.9 | C&H
6 | Window Ugine 1.5TR SEER 11.2 C | Window | UAWT18C | Ugine | 18000 | 1.5 | 11.2 | C | 6 | Window LG 1.85TR SEER 8.75 C | Window | H242EC.SN2 | LG | 22200 | 1.85 | 8.75 | C | 6 | Split_Wall_Mounted Gree 1TR SEER 15 C | Split_Wall_Mounted | GWC12AVCXD-S6DTA1C | Gree | 12000 | 1 | 15 | C | 6 | Split_Wall_Mounted Hisense 1.5TR SEER 15.25 C&H | Split_Wall_Mounted | HS18HPVI/O23 | Hisense | 18000 | 1.5 | 15.25 | C&H | 6 | Split_Wall_Mounted Hisense 2TR SEER 15.25 C V.1 | Split_Wall_Mounted | HS24C2VF/HS24C2VC | Hisense | 24000 | 2 | 15.25 | C | 6 | Split_Wall_Mounted Basic 2.28TR SEER 15.1 C&H | Split_Wall_Mounted | BSACCA-FI30HB - BSACCA-CI30HB | Basic | 27400 | 2.28 | 15.1 | C&H | 6 | Split_Floor_Standing York 4TR SEER 15.05 C&H | Split_Floor_Standing | YLKF55XL2FFB-R3M/YLKF55YL2FFBO-3M | York | 48000 | 4 | 15.05 | C&H
7 | Window TCL 1.5TR SEER 11.2 C | Window | CW-TW18CI/V1 | TCL | 18000 | 1.5 | 11.2 | C | 7 | Window Hisense 1.8TR SEER 8.65 C&H | Window | HW24HA23 | Hisense | 21600 | 1.8 | 8.65 | C&H | 7 | Split_Wall_Mounted Basic 1TR SEER 15.75 C&H V.2 | Split_Wall_Mounted | BSACMA‐FI12HB / BSACMA‐CI12HB | Basic | 12000 | 1 | 15.75 | C&H | 7 | Split_Wall_Mounted Basic 1.5TR SEER 15.3 C&H | Split_Wall_Mounted | BSACMA‐FI18HB / BSACMA‐CI18HB | Basic | 18000 | 1.5 | 15.3 | C&H | 7 | Split_Wall_Mounted Gree 2TR SEER 16.1 C | Split_Wall_Mounted | GWC24AVEXF-S6DTA1E | Gree | 24000 | 2 | 16.1 | C | 7 | Split_Wall_Mounted Haier 2.28TR SEER 15 C&H | Split_Wall_Mounted | HSU‐30HPA13/R2 (T3DBN-B) | Haier | 27400 | 2.28 | 15 | C&H | 7 | Split_Floor_Standing York 4.58TR SEER 13.9 C&H | Split_Floor_Standing | YLKF65XL2EFB‐R3M / YLKF65YL2EFBO‐3M | York | 55000 | 4.58 | 13.9 | C&H
8 | Window Zamil 1.5TR SEER 11.15 C&H V.2 | Window | RHT18CSEDMNNW | Zamil | 18000 | 1.5 | 11.15 | C&H | 8 | Window LG 1.81TR SEER 8.65 C&H | Window | H242EH.SN2 | LG | 21700 | 1.81 | 8.65 | C&H | 8 | Split_Wall_Mounted Zamil 1.03TR SEER 15.1 C&H V.1 | Split_Wall_Mounted | TSZ12EHITY | Zamil | 12300 | 1.03 | 15.1 | C&H | 8 | Split_Wall_Mounted TCL 1.53TR SEER 15 C | Split_Wall_Mounted | TAC-18CSU/TPXI11 | TCL | 18400 | 1.53 | 15 | C | 8 | Split_Wall_Mounted Gree 2TR SEER 15.75 C | Split_Wall_Mounted | GWC24AWEXF-S6DTA3A | Gree | 24000 | 2 | 15.75 | C | 8 | Split_Wall_Mounted Airfel 2.42TR SEER 15 C | Split_Wall_Mounted | LXTYEQ32VLK MXYEQ32VLKW | Airfel | 29000 | 2.42 | 15 | C | 8 | Split_Floor_Standing LG 3.83TR SEER 15.05 C&H V.2 | Split_Floor_Standing | APNW55GT3M7 / AUUW55GT7 | LG | 46000 | 3.83 | 15.05 | C&H
9 | Window TCL 1.5TR SEER 11.15 C&H | Window | CW‐TW18HI/V1 | TCL | 18000 | 1.5 | 11.15 | C&H | 9 | Window Midea 1.68TR SEER 11.15 C&H | Window | WDV24HWG | Midea | 20200 | 1.68 | 11.15 | C&H | 9 | Split_Wall_Mounted LG 1TR SEER 15.1 C V.2 | Split_Wall_Mounted | NF122C0.UJ1 | LG | 12000 | 1 | 15.1 | C | 9 | Split_Wall_Mounted York 1.5TR SEER 15.05 C&H | Split_Wall_Mounted | YHQE18XT2CHS-R5-YHQE18YT2CHSO-5 | York | 18000 | 1.5 | 15.05 | C&H | 9 | Split_Wall_Mounted Gree 2TR SEER 16.05 C&H | Split_Wall_Mounted | GWH24AVEXF‐S6DTA1B | Gree | 24000 | 2 | 16.05 | C&H | 9 | Split_Wall_Mounted Midea 2.42TR SEER 15 C&H | Split_Wall_Mounted | MSTMXV36HRNMB | Midea | 29000 | 2.42 | 15 | C&H | 9 | Split_Floor_Standing Basic 4TR SEER 15.05 C&H V.2 | Split_Floor_Standing | BVAC‐FH48HPIB1 - BVAC‐CH48HPIB1 | Basic | 48000 | 4 | 15.05 | C&H
10 |  |  | Add new item here if model not in the list | [5 empty] | 10 | Window Midea 2.02TR SEER 10.6 C | Window | WDV25CWG | Midea | 24200 | 2.02 | 10.6 | C | 10 | Split_Wall_Mounted LG 1TR SEER 15.1 C&H | Split_Wall_Mounted | NF122H0.UJ1 | LG | 12000 | 1 | 15.1 | C&H | 10 | Split_Wall_Mounted LG 1.5TR SEER 15.2 C V.2 | Split_Wall_Mounted | NS182C2 NK2 / NS182C2 UK2 | LG | 18000 | 1.5 | 15.2 | C | 10 | Split_Wall_Mounted Gree 2TR SEER 15.1 C&H | Split_Wall_Mounted | GWH24AWEXF-S6DTA3A | Gree | 24000 | 2 | 15.1 | C&H | 10 | Split_Wall_Mounted LG 2.5TR SEER 15.25 C V.1 | Split_Wall_Mounted | NT382C2NR0/UR0 | LG | 30000 | 2.5 | 15.25 | C | 10 | Split_Floor_Standing Basic 4.58TR SEER 13.9 C&H V.2 | Split_Floor_Standing | BVAC‐FH60HPIC1 - BVAC‐CH60HPIC1 | Basic | 55000 | 4.58 | 13.9 | C&H
[9 empty] | 11 | Window Zamil 1.8TR SEER 8.6 C V.1 | Window | LCH24CGXFMNNW1 | Zamil | 21600 | 1.8 | 8.6 | C | 11 | Split_Wall_Mounted Carrier 0.97TR SEER 15.65 C&H | Split_Wall_Mounted | 42QHG012VS 38QHG012VS | Carrier | 11600 | 0.97 | 15.65 | C&H | 11 | Split_Wall_Mounted LG 1.5TR SEER 15.2 C&H V.1 | Split_Wall_Mounted | NS182H2 NK2 / NS182H2 UK2 | LG | 18000 | 1.5 | 15.2 | C&H | 11 | Split_Wall_Mounted Midea 1.75TR SEER 15.05 C&H | Split_Wall_Mounted | MSTMXV24HRN2AG1 | Midea | 21000 | 1.75 | 15.05 | C&H | 11 | Split_Wall_Mounted Gree 2.5TR SEER 15.5 C | Split_Wall_Mounted | GWC30AVEXH-S6DTA1B | Gree | 30000 | 2.5 | 15.5 | C | 11 | Split_Floor_Standing Fisher 4TR SEER 15.05 C&H | Split_Floor_Standing | FVAC‐FH48HPIB1 - FVAC‐CH48HPIB1 | Fisher | 48000 | 4 | 15.05 | C&H
[9 empty] | 12 | Window Zamil 1.75TR SEER 8.65 C | Window | ZCM24CGXFMNNW1 | Zamil | 21000 | 1.75 | 8.65 | C | 12 | Split_Wall_Mounted Zamil 1TR SEER 15.85 C | Split_Wall_Mounted | AIZ12ECIZBK AKZ12EIBCJZBK | Zamil | 12000 | 1 | 15.85 | C | 12 | Split_Wall_Mounted Carrier 1.45TR SEER 15 C&H | Split_Wall_Mounted | 42QHG018VS 38QHG018VS | Carrier | 17400 | 1.45 | 15 | C&H | 12 | Split_Wall_Mounted York 1.83TR SEER 15.05 C&H | Split_Wall_Mounted | YHQE24XT2CHS-R5/YHQE24YT2CHSO-5 | York | 22000 | 1.83 | 15.05 | C&H | 12 | Split_Wall_Mounted LG 2.5TR SEER 15.25 C | Split_Wall_Mounted | NT382C2NR2 | LG | 30000 | 2.5 | 15.25 | C | 12 | Split_Floor_Standing Fisher 4.58TR SEER 13.9 C&H | Split_Floor_Standing | FVAC‐FH60HPIC1 - FVAC‐CH60HPIC1 | Fisher | 55000 | 4.58 | 13.9 | C&H
[9 empty] | 13 | Window Zamil 1.73TR SEER 8.65 C&H | Window | ZHM24CGEFMNNW1 | Zamil | 20800 | 1.73 | 8.65 | C&H | 13 | Split_Wall_Mounted Zamil 1TR SEER 15.75 C&H | Split_Wall_Mounted | AIZ12EHIZBK AKZ12EIBHJZBK | Zamil | 12000 | 1 | 15.75 | C&H | 13 | Split_Wall_Mounted Zamil 1.5TR SEER 15.3 C | Split_Wall_Mounted | AIZ18ECIZBK AKZ18EIBCJZBK | Zamil | 18000 | 1.5 | 15.3 | C | 13 | Split_Wall_Mounted LG 1.75TR SEER 15.25 C&H | Split_Wall_Mounted | NS242H3 NK2 NS242H3 UK2 | LG | 21000 | 1.75 | 15.25 | C&H | 13 | Split_Wall_Mounted Gree 2.5TR SEER 15.4 C V.1 | Split_Wall_Mounted | GWC30AWEXH-S6DTA3A | Gree | 30000 | 2.5 | 15.4 | C | 13 | Split_Floor_Standing Hisense 4.58TR SEER 13.9 C&H | Split_Floor_Standing | HUF60HAI/O23 | Hisense | 55000 | 4.58 | 13.9 | C&H
[9 empty] | 14 | Window Zamil 1.8TR SEER 8.6 C V.2 | Window | ZCP24CRXFMKHW | Zamil | 21600 | 1.8 | 8.6 | C | 14 | Split_Wall_Mounted Zamil 1.03TR SEER 15.1 C&H V.2 | Split_Wall_Mounted | TIZ12EHITBK TKZ12EIGHJTBK | Zamil | 12300 | 1.03 | 15.1 | C&H | 14 | Split_Wall_Mounted Zamil 1.5TR SEER 15.3 C&H | Split_Wall_Mounted | AIZ18EHIZBK AKZ18EIBHJZBK | Zamil | 18000 | 1.5 | 15.3 | C&H | 14 | Split_Wall_Mounted Carrier 1.75TR SEER 15 C&H | Split_Wall_Mounted | 42QHG024VS 38QHG024VS | Carrier | 21000 | 1.75 | 15 | C&H | 14 | Split_Wall_Mounted Gree 2.5TR SEER 15.5 C&H | Split_Wall_Mounted | GWH30AVEXH‐S6DTA1B | Gree | 30000 | 2.5 | 15.5 | C&H | 14 | Split_Floor_Standing LG 4TR SEER 15.25 C&H | Split_Floor_Standing | APNQ55GT3MA / APUQ55GT3MA | LG | 48000 | 4 | 15.25 | C&H
[9 empty] | 15 | Window Zamil 1.8TR SEER 8.6 C&H V.2 | Window | ZHP24CREFMKHW | Zamil | 21600 | 1.8 | 8.6 | C&H | 15 | Split_Wall_Mounted TCL 1TR SEER 15.2 C | Split_Wall_Mounted | TAC-12CSU/TSSI1 | TCL | 12000 | 1 | 15.2 | C | 15 | Split_Wall_Mounted Zamil 1.5TR SEER 15.05 C V.2 | Split_Wall_Mounted | HIZ18ECIPBK HKZ18EIGCJPBK | Zamil | 18000 | 1.5 | 15.05 | C | 15 | Split_Wall_Mounted LG 1.79TR SEER 15.35 C V.1 | Split_Wall_Mounted | NS242C3 NK2 NS242C3 UK2 | LG | 21500 | 1.79 | 15.35 | C | 15 | Split_Wall_Mounted Basic 2.62TR SEER 15 C&H | Split_Wall_Mounted | BSACCA‐FI36HB / BSACCA‐CI36HB | Basic | 31400 | 2.62 | 15 | C&H | 15 |  |  | Add new item here if model not in the list
[9 empty] | 16 | Window Ugine 1.72TR SEER 10.5 C | Window | UAWT24C | Ugine | 20600 | 1.72 | 10.5 | C | 16 | Split_Wall_Mounted TCL 1.03TR SEER 15.1 C&H | Split_Wall_Mounted | TAC-12HSU/TSSI1 | TCL | 12400 | 1.03 | 15.1 | C&H | 16 | Split_Wall_Mounted Zamil 1.5TR SEER 15.05 C&H | Split_Wall_Mounted | HIZ18EHIPBK HKZ18EIGHJPBK | Zamil | 18000 | 1.5 | 15.05 | C&H | 16 | Split_Wall_Mounted Zamil 1.83TR SEER 15.05 C V.2 | Split_Wall_Mounted | AIZ24ECIZBK AKZ24EIBCJZBK | Zamil | 22000 | 1.83 | 15.05 | C | 16 | Split_Wall_Mounted York 2.85TR SEER 15 C | Split_Wall_Mounted | YHQE36YT2CHSO-5 / YHQE36XT2CHS-R5 | York | 34200 | 2.85 | 15 | C | 16 |  |  | Add new item here if model not in the list
[9 empty] | 17 | Window Zamil 1.72TR SEER 10.5 C | Window | RCT24C | Zamil | 20600 | 1.72 | 10.5 | C | 17 | Split_Wall_Mounted Gree 0.98TR SEER 15 C | Split_Wall_Mounted | GWC12AGC-S3DTA1C | Gree | 11700 | 0.98 | 15 | C | 17 | Split_Wall_Mounted Zamil 1.53TR SEER 15.15 C | Split_Wall_Mounted | TIZ18ECITBK TKZ18EIGCJTBK | Zamil | 18400 | 1.53 | 15.15 | C | 17 | Split_Wall_Mounted Zamil 1.77TR SEER 15.05 C&H | Split_Wall_Mounted | AIZ24EHIZBK AKZ24EIBHJZBK | Zamil | 21200 | 1.77 | 15.05 | C&H | 17 | Split_Wall_Mounted Basic 2.85TR SEER 15.5 C | Split_Wall_Mounted | GWC36QFXH‐S6DTB4B | Basic | 34200 | 2.85 | 15.5 | C
[9 empty] | 18 | Window TCL 1.67TR SEER 8.6 C | Window | CW-TW24CW1 | TCL | 20000 | 1.67 | 8.6 | C | 18 | Split_Wall_Mounted Gree 0.98TR SEER 15 C&H | Split_Wall_Mounted | GWH12AGC-S3DTA1C | Gree | 11700 | 0.98 | 15 | C&H | 18 | Split_Wall_Mounted LG. 1.5TR SEER 15.2 C | Split_Wall_Mounted | NW182C0.NK0/UK0 | LG. | 18000 | 1.5 | 15.2 | C | 18 | Split_Wall_Mounted Zamil 1.83TR SEER 15.05 C | Split_Wall_Mounted | HIZ24ECIPBK HKZ24EIGCJPBK | Zamil | 22000 | 1.83 | 15.05 | C | 18 | Split_Wall_Mounted York 2.85TR SEER 15.05 C&H | Split_Wall_Mounted | YGQE36XT2B2S-R4 / YGQE36YT2B2SO-4 | York | 34200 | 2.85 | 15.05 | C&H
[9 empty] | 19 | Window TCL 1.67TR SEER 8.6 C&H | Window | CW-TW24HW1 | TCL | 20000 | 1.67 | 8.6 | C&H | 19 | Split_Wall_Mounted Gree 1TR SEER 15 C&H | Split_Wall_Mounted | GWH12AWCXB-S6DTA3A | Gree | 12000 | 1 | 15 | C&H | 19 | Split_Wall_Mounted LG 1.5TR SEER 15.2 C&H V.2 | Split_Wall_Mounted | NW182H0.NK0/UK0 | LG | 18000 | 1.5 | 15.2 | C&H | 19 | Split_Wall_Mounted Zamil 1.83TR SEER 15.05 C&H | Split_Wall_Mounted | HIZ24EHIPBK HKZ24EIGHJPBK | Zamil | 22000 | 1.83 | 15.05 | C&H | 19 | Split_Wall_Mounted York 2.28TR SEER 15 C&H | Split_Wall_Mounted | YHQE30YT2CHSO-5 / YHQE30XT2CHS-R5 | York | 27400 | 2.28 | 15 | C&H
[9 empty] | 20 | Window TCL 1.72TR SEER 10.3 C | Window | CW-TW24CI/V1 | TCL | 20600 | 1.72 | 10.3 | C | 20 | Split_Wall_Mounted Basic 1TR SEER 15.85 C V.2 | Split_Wall_Mounted | BSACMA‐FI12CB BSACMA‐CI12CB | Basic | 12000 | 1 | 15.85 | C | 20 | Split_Wall_Mounted Midea 1.5TR SEER 15.25 C&H | Split_Wall_Mounted | MSTXCV18HRNXT | Midea | 18000 | 1.5 | 15.25 | C&H | 20 | Split_Wall_Mounted LG 1.79TR SEER 15.35 C V.2 | Split_Wall_Mounted | NW242C0.NK0/UK0 | LG | 21500 | 1.79 | 15.35 | C | 20 | Split_Wall_Mounted Fisher 2.28TR SEER 15.1 C&H | Split_Wall_Mounted | FSACCA-XF30HIB / FSACCA-XC30HIB | Fisher | 27400 | 2.28 | 15.1 | C&H
[9 empty] | 21 | Window Fisher 1.82TR SEER 8.65 C | Window | FWAC‐H24CF | Fisher | 21800 | 1.82 | 8.65 | C | 21 | Split_Wall_Mounted Basic 1TR SEER 15.15 C | Split_Wall_Mounted | BSACMA‐FI12CB/B BSACMA‐CI12CB/B | Basic | 12000 | 1 | 15.15 | C | 21 | Split_Wall_Mounted Fisher 1.5TR SEER 15.3 C | Split_Wall_Mounted | FSACME‐XF18CIB FSACME‐XC18CIB | Fisher | 18000 | 1.5 | 15.3 | C | 21 | Split_Wall_Mounted LG 1.75TR SEER 15.25 C&H V.2 | Split_Wall_Mounted | NW242H0.NK0/UK0 | LG | 21000 | 1.75 | 15.25 | C&H | 21 | Split_Wall_Mounted LG 2.5TR SEER 15.25 C V.2 | Split_Wall_Mounted | NT382C2 NR2 / NT382C2 UR2 | LG | 30000 | 2.5 | 15.25 | C
[9 empty] | 22 | Window Fisher 1.8TR SEER 8.65 C&H | Window | FWAC‐H24HF | Fisher | 21600 | 1.8 | 8.65 | C&H | 22 | Split_Wall_Mounted Basic 1TR SEER 15.15 C&H | Split_Wall_Mounted | BSACMA‐FI12HB/B BSACMA‐CI12HB/B | Basic | 12000 | 1 | 15.15 | C&H | 22 | Split_Wall_Mounted Basic 1.6TR SEER 15.05 C | Split_Wall_Mounted | BSACMA‐FI19CB/B - BSACMA‐CI19CB/B | Basic | 19200 | 1.6 | 15.05 | C | 22 | Split_Wall_Mounted Midea 1.79TR SEER 15.05 C&H | Split_Wall_Mounted | MSTXCV24HRNXT | Midea | 21500 | 1.79 | 15.05 | C&H | 22 | Split_Wall_Mounted LG 2.5TR SEER 15.25 C&H | Split_Wall_Mounted | NT382H2.NR2 | LG | 30000 | 2.5 | 15.25 | C&H
[9 empty] | 23 | Window York 1.8TR SEER 8.6 C&H | Window | YWHE24ZH2DHCOR3 | York | 21600 | 1.8 | 8.6 | C&H | 23 | Split_Wall_Mounted Fisher 1TR SEER 15.75 C&H | Split_Wall_Mounted | FSACME‐XF12HIB FSACME‐XC12HIB | Fisher | 12000 | 1 | 15.75 | C&H | 23 | Split_Wall_Mounted Basic 1.6TR SEER 15.05 C&H | Split_Wall_Mounted | BSACMA‐FI19HB/B - BSACMA‐CI19HB/B | Basic | 19200 | 1.6 | 15.05 | C&H | 23 | Split_Wall_Mounted Basic 1.83TR SEER 15.05 C | Split_Wall_Mounted | BSACMA-FI24CB - BSACMA-CI24CB | Basic | 22000 | 1.83 | 15.05 | C | 23 | Split_Wall_Mounted Zamil 2.28TR SEER 15.1 C | Split_Wall_Mounted | AIZ30ECIZBK AKZ30EIBCJZBK | Zamil | 27400 | 2.28 | 15.1 | C
[9 empty] | 24 | Window Zamil 1.72TR SEER 10.5 C&H | Window | ZHT24CSEDMNW | Zamil | 20600 | 1.72 | 10.5 | C&H | 24 | Split_Wall_Mounted Fisher 1TR SEER 15.85 C | Split_Wall_Mounted | FSACME‐XF12CIB FSACME‐XC12CIB | Fisher | 12000 | 1 | 15.85 | C | 24 | Split_Wall_Mounted Fisher 1.5TR SEER 15.3 C&H | Split_Wall_Mounted | FSACME‐XF18HIB FSACME‐XC18HIB | Fisher | 18000 | 1.5 | 15.3 | C&H | 24 | Split_Wall_Mounted Basic 2TR SEER 15.1 C | Split_Wall_Mounted | BSACMA‐FI24CB/B - BSACMA‐CI24CB/B | Basic | 24000 | 2 | 15.1 | C | 24 | Split_Wall_Mounted Zamil 2.28TR SEER 15.1 C&H | Split_Wall_Mounted | AIZ30EHIZBK AKZ30EIBHJZBK | Zamil | 27400 | 2.28 | 15.1 | C&H
[9 empty] | 25 | Window Haier 1.79TR SEER 8.6 C | Window | HW-24LWA13/R2(T3) | Haier | 21500 | 1.79 | 8.6 | C | 25 | Split_Wall_Mounted Daikin 1.1TR SEER 16.85 C&H | Split_Wall_Mounted | FTHF12TVMVZK/RHFG12TVMVZK | Daikin | 13200 | 1.1 | 16.85 | C&H | 25 | Split_Wall_Mounted Gree 1.5TR SEER 15.05 C V.1 | Split_Wall_Mounted | GWC18AGD-S3DTA1A | Gree | 18000 | 1.5 | 15.05 | C | 25 | Split_Wall_Mounted Basic 2TR SEER 15.05 C&H | Split_Wall_Mounted | BSACMA‐FI24HB/B - BSACMA‐CI24HB/B | Basic | 24000 | 2 | 15.05 | C&H | 25 | Split_Wall_Mounted Zamil 2.62TR SEER 15 C | Split_Wall_Mounted | AIZ36ECIZBK AKZ36EIBCJZBK | Zamil | 31400 | 2.62 | 15 | C
[9 empty] | 26 | Window Haier 1.79TR SEER 8.6 C&H | Window | HW-24EWA13/R2(T3) | Haier | 21500 | 1.79 | 8.6 | C&H | 26 | Split_Wall_Mounted Daikin 1.1TR SEER 17.1 C | Split_Wall_Mounted | FTKF12TVMVZK/RKFG12TVMVZK | Daikin | 13200 | 1.1 | 17.1 | C | 26 | Split_Wall_Mounted Gree 1.5TR SEER 15.05 C&H V.1 | Split_Wall_Mounted | GWH18AGD-S3DTA1A | Gree | 18000 | 1.5 | 15.05 | C&H | 26 | Split_Wall_Mounted Fisher 1.83TR SEER 15.05 C | Split_Wall_Mounted | FSACME‐XF24CIB FSACME‐XC24CIB | Fisher | 22000 | 1.83 | 15.05 | C | 26 | Split_Wall_Mounted Zamil 2.62TR SEER 15 C&H | Split_Wall_Mounted | AIZ36EHIZBK AKZ36EIBHJZBK | Zamil | 31400 | 2.62 | 15 | C&H
[9 empty] | 27 | Window Ugine 1.75TR SEER 8.65 C | Window | UAWMS24C | Ugine | 21000 | 1.75 | 8.65 | C | 27 | Split_Wall_Mounted Ugine 1.01TR SEER 15 C | Split_Wall_Mounted | UAST12C4 | Ugine | 12100 | 1.01 | 15 | C | 27 | Split_Wall_Mounted Gree 1.5TR SEER 15.05 C&H V.2 | Split_Wall_Mounted | GWH18AWDXE‐S6DTA3B | Gree | 18000 | 1.5 | 15.05 | C&H | 27 | Split_Wall_Mounted Fisher 1.77TR SEER 15.05 C&H | Split_Wall_Mounted | FSACME‐XF24HIB FSACME‐XC24HIB | Fisher | 21200 | 1.77 | 15.05 | C&H | 27 | Split_Wall_Mounted Zamil 2.28TR SEER 15 C V.2 | Split_Wall_Mounted | HIZ30ECIPBK HKZ30EIGCJPBK | Zamil | 27400 | 2.28 | 15 | C
[9 empty] | 28 |  |  | Add new item here if model not in the list | [5 empty] | 28 | Split_Wall_Mounted Airfel 1.03TR SEER 15.1 C&H | Split_Wall_Mounted | LXTYGQ12VLK / MXYGQ12VLKW | Airfel | 12300 | 1.03 | 15.1 | C&H | 28 | Split_Wall_Mounted Gree 1.5TR SEER 15.05 C V.2 | Split_Wall_Mounted | GWC18AWDXE‐S6DTA3B | Gree | 18000 | 1.5 | 15.05 | C | 28 | Split_Wall_Mounted Hisense 2TR SEER 15.25 C V.2 | Split_Wall_Mounted | HS24CPVI23 / HS24CPVO23 | Hisense | 24000 | 2 | 15.25 | C | 28 | Split_Wall_Mounted Zamil 2.28TR SEER 15 C&H | Split_Wall_Mounted | HIZ30EHIPBK HKZ30EIGHJPBK | Zamil | 27400 | 2.28 | 15 | C&H
[18 empty] | 29 |  |  | Add new item here if model not in the list | [5 empty] | 29 | Split_Wall_Mounted Hisense 1.5TR SEER 15.45 C | Split_Wall_Mounted | HS18CPVI/O23 | Hisense | 18000 | 1.5 | 15.45 | C | 29 | Split_Wall_Mounted Hisense 2TR SEER 15.25 C&H | Split_Wall_Mounted | HS24HPVI23/HS24HPVO23 | Hisense | 24000 | 2 | 15.25 | C&H | 29 | Split_Wall_Mounted Fisher 2.62TR SEER 15 C | Split_Wall_Mounted | FSACCA‐XF36CIB FSACCA‐XC36CIB | Fisher | 31400 | 2.62 | 15 | C
[18 empty] | 30 | [8 empty] | 30 | Split_Wall_Mounted Airfel 1.47TR SEER 15.75 C&H | Split_Wall_Mounted | LXTYEQ18VLK/MXYEQ18VLKW | Airfel | 17600 | 1.47 | 15.75 | C&H | 30 | Split_Wall_Mounted Gree 2TR SEER 15.8 C&H | Split_Wall_Mounted | GWC24AWEXF-S6DTA3F | Gree | 24000 | 2 | 15.8 | C&H | 30 | Split_Wall_Mounted Fisher 2.62TR SEER 15 C&H | Split_Wall_Mounted | FSACCA‐XF36HIB FSACCA‐XC36HIB | Fisher | 31400 | 2.62 | 15 | C&H
[27 empty] | 31 | Split_Wall_Mounted Haier 1.5TR SEER 15.05 C&H | Split_Wall_Mounted | HSU-18HPA13/R2(T3DB) | Haier | 18000 | 1.5 | 15.05 | C&H | 31 | Split_Wall_Mounted Haier 1.83TR SEER 15.05 C | Split_Wall_Mounted | HSU-24LPA13/R2(T3DB) | Haier | 22000 | 1.83 | 15.05 | C | 31 | Split_Wall_Mounted Basic 2.62TR SEER 15 C | Split_Wall_Mounted | BSACCA‐FI36CB BSACCA‐CI36CB | Basic | 31400 | 2.62 | 15 | C
[27 empty] | 32 | Split_Wall_Mounted Haier 1.5TR SEER 15.05 C | Split_Wall_Mounted | HSU-18LPA13/R2(T3DB) | Haier | 18000 | 1.5 | 15.05 | C | 32 | Split_Ceiling_Cassette Hisense 1.91TR SEER 15.85 C&H | Split_Ceiling_Cassette | HUC24HI23/O23 | Hisense | 22900 | 1.91 | 15.85 | C&H | 32 | Split_Wall_Mounted Basic 2.28TR SEER 15.1 C | Split_Wall_Mounted | BSACCA‐FI30CB - BSACCA‐CI30CB | Basic | 27400 | 2.28 | 15.1 | C
[27 empty] | 33 | Split_Ceiling_Cassette Fuji 1.5TR SEER 17 C&H | Split_Ceiling_Cassette | RCH18KRTA-S ROH18KBTB-S | Fuji | 18000 | 1.5 | 17 | C&H | 33 | Split_Wall_Mounted Haier 1.83TR SEER 15.05 C&H | Split_Wall_Mounted | HSU-24HPA13/R2(T3DB) | Haier | 22000 | 1.83 | 15.05 | C&H | 33 | Split_Wall_Mounted Gree 2.5TR SEER 15.4 C V.2 | Split_Wall_Mounted | GWC30AWEXH‐S6DTA3A/I GWC30AWEXH‐S6DTA1A/O | Gree | 30000 | 2.5 | 15.4 | C
[27 empty] | 34 | Split_Wall_Mounted Ugine 1.5TR SEER 15.65 C | Split_Wall_Mounted | UASMINV18C | Ugine | 18000 | 1.5 | 15.65 | C | 34 | Split_Wall_Mounted Ugine 1.93TR SEER 15.95 C | Split_Wall_Mounted | UASMINV24C | Ugine | 23200 | 1.93 | 15.95 | C | 34 | Split_Wall_Mounted Basic 2.5TR SEER 15 C V.1 | Split_Wall_Mounted | BSACCA‐FI30CB/B BSACCA‐CI30CB/B | Basic | 30000 | 2.5 | 15 | C
[27 empty] | 35 | Split_Wall_Mounted Basic 1.5TR SEER 15.05 C&H | Split_Wall_Mounted | BSACMA‐FI18HBN BSACMA‐CI18HBN | Basic | 18000 | 1.5 | 15.05 | C&H | 35 | Split_Wall_Mounted Airfel 1.75TR SEER 15 C&H | Split_Wall_Mounted | LXTYGQ24VLK‐SP1 / MXYGQ24VLKW‐SP1 | Airfel | 21000 | 1.75 | 15 | C&H | 35 | Split_Wall_Mounted Airfel 2.42TR SEER 15 C&H | Split_Wall_Mounted | LXTYEQ32VLK/MXYEQ32VLKW | Airfel | 29000 | 2.42 | 15 | C&H
[27 empty] | 36 | Split_Wall_Mounted Airfel 1.48TR SEER 15 C&H | Split_Wall_Mounted | LXTYGQ18VLK‐SP1 / MXYGQ18VLKW‐SP1 | Airfel | 17800 | 1.48 | 15 | C&H | 36 |  |  | Add new item here if model not in the list | [5 empty] | 36 | Split_Wall_Mounted Haier 2.28TR SEER 15 C | Split_Wall_Mounted | HSU-30LPA13/R2(T3DB) | Haier | 27400 | 2.28 | 15 | C
[27 empty] | 37 | Split_Wall_Mounted Basic 1.5TR SEER 15.05 C&H | Split_Wall_Mounted | BSACMA‐FI18HBN / BSACMA‐CI18HBN | Basic | 18000 | 1.5 | 15.05 | C&H | 37 |  |  | Add new item here if model not in the list | [5 empty] | 37 | Split_Wall_Mounted Haier 2.75TR SEER 15.05 C&H | Split_Wall_Mounted | HSU-36HPA13/R2(T3DB) | Haier | 33000 | 2.75 | 15.05 | C&H
[27 empty] | 38 |  |  | Add new item here if model not in the list | [14 empty] | 38 | Split_Wall_Mounted Basic 2.33TR SEER 15 C&H | Split_Wall_Mounted | BSACMA-FI30HB/B | Basic | 28000 | 2.33 | 15 | C&H
[27 empty] | 39 |  |  | Add new item here if model not in the list | [14 empty] | 39 | Split_Wall_Mounted Basic 2.33TR SEER 15.75 C&H | Split_Wall_Mounted | BSACCA‐FI30HB/B BSACCA‐CI30HB/B | Basic | 28000 | 2.33 | 15.75 | C&H
[45 empty] | 40 | Split_Ceiling_Cassette Fuji 2.5TR SEER 15.9 C&H | Split_Ceiling_Cassette | RCH30KRTA‐S/ROH30KBTB‐S | Fuji | 30000 | 2.5 | 15.9 | C&H
[45 empty] | 41 | Split_Ceiling_Cassette Fuji 2.92TR SEER 15.65 C&H | Split_Ceiling_Cassette | RCH36KRTA-S ROH36KBTB-S | Fuji | 35000 | 2.92 | 15.65 | C&H
[45 empty] | 42 | Split_Wall_Mounted Basic 2.5TR SEER 15 C V.2 | Split_Wall_Mounted | BSACCA‐FI30CB/B - BSACCA‐CI30CB/B | Basic | 30000 | 2.5 | 15 | C
[45 empty] | 43 | Split_Wall_Mounted Basic 3TR SEER 15 C | Split_Wall_Mounted | BSACCA‐FI36CB/B - BSACCA‐CI36CB/B | Basic | 36000 | 3 | 15 | C
[45 empty] | 44 | Split_Wall_Mounted Basic 2.93TR SEER 15.15 C&H | Split_Wall_Mounted | BSACCA‐FI36HB/B - BSACCA‐CI36HB/B | Basic | 35200 | 2.93 | 15.15 | C&H
[45 empty] | 45 |  |  | Add new item here if model not in the list
[45 empty] | 46 |  |  | Add new item here if model not in the list
[45 empty] | 47 |  |  | Add new item here if model not in the list